## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of DISTINCT_UNITS | Sum of EVENT_COUNT | Sum of MWLost | Sum of MWHrsLost
0010-Thaw shed failure or fire | 10 | 10 | 371 | 2863.5832
0020-Coal car dumpers; shakers; and unloaders | 7 | 7 | 994.3 | 2818.7328
0022-Unloading/receiving hopper (train/truck) | 1 | 1 | 19.9 | 53.0667
0024-Rotary plow | 6 | 6 | 621 | 11310.4498
0028-Dust collection system | 6 | 6 | 1274.6 | 60625.2494
0030-Coal conveyors and feeders | 224 | 225 | 45265.87 | 471875.0976
0035-Metal detector/collector (including magnetic separator) | 5 | 5 | 601.27 | 464.6496
0040-Coal elevators | 3 | 3 | 176.57 | 1089.2011
0060-Coal crushers including motors | 17 | 17 | 1739.44 | 21411.0378
0075-Storage silos/hoppers | 14 | 14 | 1502.77 | 5726.8857
0080-Stackers/reclaimers | 41 | 41 | 4394.83 | 28255.6876
0084-Coal conveyor scales-storage coal pile | 9 | 9 | 315.9 | 7446.7416
0085-Bunker feeder coal scales | 2 | 2 | 195.89 | 1799.3099
0090-Bunker fires | 10 | 10 | 1349.88 | 102940.846
0095-Bunker flow problems | 227 | 228 | 14071.99 | 105585.4462
0100-Bunker gates | 14 | 14 | 593.49 | 5928.8337
0105-Bunker structures | 10 | 10 | 486.71 | 2037.5298
0107-Screen (prior to bunkers) | 1 | 1 | 120 | 319.9999
0110-Other coal fuel supply problems up through bunkers | 79 | 79 | 15396.65 | 108802.565
0111-Solid fuel feeder conveyors | 65 | 67 | 1871.79 | 12920.3164
0114-Solid fuel volumetric feeder | 45 | 45 | 736.1 | 5424.0297
0115-Solid fuel gravimetric feeder | 13 | 13 | 632.7 | 7461.9682
0116-Solid fuel feeder motors | 2 | 2 | 38.7 | 1546.6667
0121-Other solid fuel feed problems | 23 | 23 | 1620.45 | 7691.2338
0125-Coal crusher dryer hammers | 2 | 2 | 136 | 412.5333
0129-Other coal processing system problems | 33 | 33 | 5173.37 | 44470.3133
0150-Sorbent feed conveyors | 1 | 1 | 20 | 380
0156-Other sorbent feed problems | 3 | 3 | 93 | 339.4666
0163-Bed material feeders | 2 | 2 | 16.4 | 841.54
0200-Pulverizer exhauster fan (for indirect firing) | 15 | 15 | 975.22 | 41215.8907
0205-Pulverizer exhauster fan drive | 12 | 12 | 1270 | 13949.1165
0240-Pulverized coal bin | 27 | 27 | 6241 | 44082.4638
0250-Pulverizer feeders | 1229 | 1230 | 135382.98 | 1070673.4452
0253-Pulverizer feeder motor | 35 | 35 | 3545.5 | 33569.8962
0255-Pulverizer feeder coal scales | 11 | 11 | 1084.79 | 2807.565
0256-Seal air system (air to pulverizers) | 17 | 17 | 2355.72 | 26932.8799
0257-Coal Crusher/dryer between feeder and pulverizer | 4 | 4 | 501.98 | 1310.2915
0260-Primary air fan | 126 | 126 | 20798.98 | 1911064.6569
0262-Primary air fan lube oil system | 20 | 20 | 5548.64 | 43636.4481
0263-Primary air fan drives | 34 | 35 | 5095 | 73931.9816
0264-Other primary air fan problems | 36 | 36 | 7365 | 173852.1604
0265-Primary air heater | 8 | 8 | 2139.76 | 45056.3448
0266-Primary air heater fouling | 4 | 4 | 104 | 11008.25
0267-Primary air flow instrumentation | 40 | 40 | 4621.59 | 38349.7058
0270-Primary air duct and dampers | 129 | 129 | 20786.78 | 792349.2341
0280-Pulverizer fires | 52 | 52 | 6897.92 | 159810.0048
0290-Pulverizer reduced capacity due to wear | 14 | 14 | 882.9 | 20746.138
0300-Pulverizer motors and drives | 96 | 96 | 8612.02 | 425076.9775
0310-Pulverizer mills | 869 | 870 | 89827.74 | 1894050.0933
0312-Pulverizer mill classifiers | 33 | 33 | 4368.2 | 105065.4945
0313-Pulverizer mill trunnion seals | 8 | 8 | 787.76 | 9512.023
0315-Pulverizer mill coal level controls | 17 | 17 | 1231.67 | 4718.3763
0320-Foreign object in Pulverizers mill | 88 | 88 | 6221.69 | 82380.5483
0325-Pulverizer skidding | 6 | 6 | 502.1 | 5356.0031
0330-Pulverizer coal leak (pulverizers only) | 126 | 126 | 12762.35 | 86516.7682
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 62 | 62 | 7361.49 | 66403.0723
0335-Pulverizer lube oil system | 164 | 164 | 17018.07 | 124622.2277
0338-Pulverizer control systems (temperature and pressure) | 42 | 42 | 4043.08 | 47173.052
0339-Pulverizer System Puff | 4 | 4 | 171.39 | 8419.8933
0340-Other pulverizer problems | 278 | 280 | 37181.12 | 492479.0323
0341-Pulverizer deluge system | 2 | 2 | 137.2 | 712.8333
0342-Pulverizer inert system | 12 | 12 | 2308.6 | 37671.578
0344-Pulverizer inspection | 48 | 48 | 4215.23 | 93504.4836
0345-Pulverizer overhaul | 28 | 29 | 2567.8 | 158267.4958
0346-Pulverizer pyrite removal system | 131 | 131 | 10818.83 | 71167.5967
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 75 | 75 | 7413.29 | 161684.328
0358-Oil burner piping and valves | 6 | 6 | 878.9 | 5571.6663
0359-Gas burner piping and valves | 158 | 158 | 17396.15 | 264412.1226
0360-Burners | 121 | 122 | 10015.21 | 479607.5638
0370-Burner instruments and controls (except light-off) | 97 | 97 | 12497.58 | 191150.2013
0380-Light-off (igniter) systems (including fuel supply) | 59 | 59 | 11749.28 | 243616.3197
0385-Igniters | 85 | 85 | 13500.39 | 84269.9178
0390-Burner wind boxes and dampers | 15 | 16 | 1694.24 | 19633.1095
0400-Burner wind box fires | 12 | 12 | 3408.61 | 159846.0125
0410-Other burner problems | 79 | 79 | 7443.29 | 169618.5579
0415-Cyclone feeders | 102 | 102 | 5773.21 | 78016.9565
0420-Cyclone crusher | 18 | 18 | 780 | 15988.4998
0425-Cyclone dampers | 3 | 3 | 107 | 3417.05
0426-Cyclone air ducts | 2 | 2 | 95 | 752.75
0430-Cyclone furnace | 4 | 4 | 304 | 9637.0075
0435-Other cyclone problems | 248 | 331 | 6961.68 | 40138.0042
0440-Fuel oil pumps (general) | 2 | 2 | 2130 | 32942.6658
0441-Fuel oil pumps (burner supply) | 2 | 2 | 1172.5 | 2578.7999
0460-Fuel oil atomizers | 6 | 6 | 680 | 3046.9165
0470-Oil and gas fires | 8 | 8 | 1241.2 | 11253.1792
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 60 | 61 | 11024.54 | 525006.4602
0500-Main steam piping up to turbine stop valves | 35 | 35 | 8458.38 | 1199745.0654
0510-Main steam relief/safety valves off superheater | 21 | 21 | 5275.3 | 297323.1834
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 48 | 48 | 10277.98 | 277342.9996
0530-Other main steam system problems | 70 | 76 | 4456.45 | 147120.1339
0540-Hot reheat steam piping up to turbine stop valves | 40 | 40 | 8224.8 | 238204.3536
0541-Cold reheat steam piping up to boiler | 8 | 8 | 1785.8 | 71557.5628
0550-Reheat steam relief/safety valves | 31 | 31 | 5582.59 | 211422.8675
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 29 | 29 | 7393.53 | 332475.5291
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 41 | 41 | 8991 | 83075.0637
0570-Other reheat steam problems | 53 | 56 | 5400.24 | 425014.2291
0580-Desuperheater/attemperator piping | 10 | 10 | 3028.45 | 267525.4057
0590-Desuperheater/attemperator valves | 38 | 39 | 6655.54 | 115626.3797
0620-Other desuperheater/attemperator problems | 9 | 9 | 1944.41 | 24055.1727
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 3 | 3 | 903.13 | 44133.4571
0640-Startup bypass system valves | 21 | 21 | 11873 | 933687.4789
0650-Startup bypass tanks or flash tanks | 5 | 5 | 3223.21 | 147702.6456
0655-Steam by-pass system instrumentation and controls | 1 | 1 | 658 | 1129.5662
0660-Other startup bypass system problems | 2 | 2 | 1080 | 7449.4995
0670-Feedwater piping downstream of feedwater regulating valve | 11 | 12 | 1366.1 | 92308.108
0680-Feedwater valves (not feedwater regulating valve) | 40 | 40 | 8308.61 | 152659.692
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 21 | 21 | 6639.45 | 56894.9156
0700-Blowdown system valves A | 4 | 4 | 811.27 | 3006.8423
0710-Blowdown system piping B | 6 | 6 | 1078.27 | 35175.7281
0720-Blowdown system controls / instrumentation | 6 | 6 | 1011.98 | 20351.2791
0730-Other blowdown system problems | 4 | 4 | 654.98 | 42527.403
0740-Boiler recirculation pumps | 26 | 26 | 7128.36 | 350918.5337
0741-Boiler recirculation pumps - motors | 11 | 11 | 2625 | 269082.4323
0742-Boiler recirculation pumps - motors - cooling system | 4 | 4 | 1482 | 15108.9325
0750-Boiler recirculation piping including downcomers | 11 | 11 | 3322.8 | 1454406.1654
0760-Boiler recirculation valves | 3 | 3 | 1128 | 5593.4994
0770-Other boiler recirculation problems | 6 | 6 | 720.5 | 7357.1499
0775-Economizer piping | 17 | 17 | 4427.4 | 458875.2269
0780-Headers between tube bundles | 2 | 2 | 340 | 42972.4999
0782-Headers and caps | 2 | 2 | 488.2 | 11673.0731
0790-Pipe hangers; brackets; supports (general) | 2 | 2 | 391 | 62988.2831
0799-Other miscellaneous piping system problems | 32 | 33 | 6065.15 | 244740.9653
0800-Drums and drum internals (single drum only) | 39 | 39 | 8584.27 | 135322.5703
0801-HP Drum (including drum level trips not attributable to other causes) | 109 | 109 | 19599.66 | 341881.094
0802-IP Drum (including drum level trips not attributable to other causes) | 56 | 56 | 11468.97 | 52595.4407
0803-LP Drum (including drum level trips not attributable to other causes) | 35 | 35 | 6669.86 | 48022.6818
0810-Boiler supports and structures (use code 1320 for tube supports) | 4 | 4 | 1649.92 | 1131527.1269
0820-Casing | 27 | 27 | 4460.21 | 508630.2778
0830-Doors | 26 | 26 | 3919.88 | 144815.9186
0840-Refractory and insulation | 7 | 7 | 1218.78 | 118406.7621
0845-Windbox expansion joints | 2 | 2 | 835.5 | 6682.133
0847-Other expansion joints | 10 | 10 | 1766 | 255763.3161
0850-Other internal or structural problems | 5 | 5 | 864 | 197757.8996
0855-Drum relief/safety valves (Single drum only) | 9 | 9 | 935.85 | 10692.2467
0856-HP Drum relief/safety valves | 4 | 4 | 651.55 | 25379.3863
0859-Tube external fins/membranes A | 2 | 2 | 819 | 127454.483
0860-Soot blowers - air (see code 3844 for air delivery system) | 36 | 36 | 2398.69 | 85515.2455
0870-Soot blowers - steam | 67 | 70 | 6143.78 | 62203.8563
0872-Soot blowers - water | 8 | 8 | 444.9 | 7532.8416
0873-Soot blower drives | 3 | 3 | 159 | 58.8666
0876-Soot blower controls | 21 | 21 | 2005.6 | 33382.9497
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 33 | 33 | 5988.41 | 335554.8554
0885-Fly ash Removal System - wet transport | 1 | 1 | 480 | 3312
0890-Bottom ash systems (wet or dry) | 149 | 151 | 17062.56 | 1167462.3396
0891-Bottom ash hoppers (including gates) | 68 | 69 | 9931 | 376184.7798
0892-Bottom ash clinker grinders | 23 | 23 | 5467.9 | 239286.3313
0893-Bottom ash water pumps and motors | 3 | 3 | 508 | 2314.4999
0894-Bottom ash piping and valves | 30 | 30 | 7007.7 | 128012.269
0895-Ashpit trouble | 3 | 3 | 781 | 10946.1998
0897-Bottom ash rotary (drag chain type) conveyor and motor | 99 | 99 | 28916.96 | 996984.4055
0898-Bottom ash pyrite hopper (pulverizer reject) system | 1 | 1 | 42 | 84
0899-Bottom ash controls and instrumentation | 1 | 1 | 95 | 204.25
0900-Slag-tap (cyclone furnace) | 19 | 19 | 2125.86 | 127260.4648
0910-Slag-tap (other than cyclone furnace) | 1 | 1 | 201 | 331.65
0920-Other slag and ash removal problems A | 67 | 73 | 11472.8 | 220588.6772
0930-Bed material coolers | 4 | 4 | 446.6 | 25329.3832
0933-Bed material fans/blowers | 1 | 1 | 312 | 1362.3998
0950-Other bed material system problems | 1 | 1 | 58 | 1283.7333
0971-Flue gas-solids separator piping and valves | 1 | 1 | 32.5 | 1057.3333
0980-High pressure loop seal recirculation fans/blowers | 1 | 1 | 346.7 | 3287.8716
0989-Other bed solids recirculation problems | 10 | 10 | 1614.7 | 228214.6729
0990-Refractory | 2 | 2 | 184.4 | 29368.7466
0991-Tube leaks | 16 | 16 | 1181.4 | 151546.6247
1000-Waterwall (Furnace wall) | 594 | 594 | 190881.02 | 15959006.9667
1003-Steam generating tubes between steam drum and mud drum | 9 | 9 | 3671.96 | 332109.0823
1005-Generating tubes | 23 | 23 | 4075.08 | 307837.8397
1010-Cyclone furnace (in cyclone area only) | 21 | 21 | 6125.79 | 588892.7627
1020-Convection pass wall (water tubes only) | 16 | 16 | 7533.58 | 382360.1985
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 10 | 10 | 3765 | 337446.4486
1035-Platen superheater | 36 | 36 | 14544.3 | 1513361.5106
1040-First superheater | 106 | 106 | 33059.97 | 2837580.8332
1050-Second superheater | 188 | 188 | 54929.12 | 4650425.5164
1055-External superheater link tubing | 1 | 1 | 193 | 17810.6833
1060-First reheater | 115 | 115 | 52560.84 | 4625214.4342
1070-Second reheater | 38 | 38 | 15325.15 | 1355630.6865
1075-External reheater link tubing | 2 | 2 | 648 | 684154.3996
1080-Economizer | 122 | 122 | 31567.01 | 2407365.9615
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 2 | 2 | 157.8 | 28217.27
1090-Other boiler tube leaks | 140 | 140 | 34522.47 | 3938233.9253
1100-Waterwall (Furnace wall) | 70 | 74 | 11654.34 | 1092910.1776
1103-Steam generating tubes between steam drum and mud drum | 5 | 5 | 1201.7 | 86306.9994
1105-Generating tubes | 6 | 6 | 148 | 71240.8333
1110-Cyclone furnace (in cyclone area only) | 2 | 2 | 145 | 5102.0833
1120-Convection pass wall | 3 | 3 | 1010.13 | 25389.9979
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 3 | 3 | 829 | 26266.5161
1140-First superheater | 52 | 54 | 3139.1 | 173906.917
1150-Second superheater | 89 | 94 | 10059.82 | 269035.1731
1160-First reheater | 87 | 95 | 5003.41 | 178020.6131
1170-Second reheater | 27 | 30 | 2845 | 48696.6992
1180-Economizer | 33 | 33 | 1532 | 24946.1661
1190-Other tube slagging or fouling | 54 | 54 | 3855.71 | 87060.8047
1191-Bed agglomeration (FBC only) | 4 | 4 | 279 | 4166.2
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 64 | 68 | 6803.5 | 190723.332
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 2 | 2 | 83 | 2490
1310-Water side cleaning (acid cleaning) | 1 | 1 | 440 | 50013.333
1320-Tube supports/attachments | 2 | 2 | 132.2 | 10183.0033
1330-Slag fall damage | 2 | 2 | 940 | 1776.6664
1350-Other miscellaneous boiler tube problems | 15 | 15 | 1989.27 | 445503.5478
1360-Boiler drains system | 13 | 13 | 3747 | 163765.1326
1400-Forced draft fans | 164 | 164 | 27083.9 | 2723282.4715
1401-Forced draft fan dampers | 52 | 52 | 9262.65 | 196228.8909
1407-Forced draft fan lubrication system | 16 | 16 | 4883.1 | 100399.9588
1410-Forced draft fan motors | 59 | 59 | 10322.87 | 894456.8128
1411-Forced draft fan motors - variable speed | 13 | 14 | 2942 | 32755.0324
1412-Forced draft fan drives (other than motor) | 20 | 20 | 3449.49 | 48977.74
1413-Forced draft fan couplings | 7 | 7 | 1140.82 | 72931.7767
1415-Forced draft fan controls | 49 | 49 | 7453.56 | 95635.1361
1420-Other forced draft fan problems | 79 | 80 | 11960.99 | 247062.9508
1421-Secondary air fans/blowers | 7 | 7 | 552.59 | 9361.6641
1422-Secondary air fan/blower motors - single speed | 4 | 4 | 351 | 207199.2667
1423-Secondary air fan/blower motors - variable speed | 1 | 1 | 300 | 1005
1424-Secondary air fan/blower controls | 5 | 5 | 857 | 3467.2496
1430-Air supply ducts from FD fan | 3 | 3 | 149 | 39355.3333
1431-Air supply dampers from FD fan | 8 | 8 | 1297.4 | 7755.5512
1432-Air supply duct expansion joints | 13 | 13 | 2027.83 | 513671.2676
1440-Air supply dampers | 14 | 14 | 2171.7 | 8131.9228
1450-Other air supply problems | 245 | 247 | 10966.01 | 363167.558
1451-Fluidized Air Fan | 1 | 1 | 32.5 | 32710.1666
1455-Induced draft fans | 339 | 341 | 35485.43 | 2627005.4962
1456-Induced draft fan dampers | 54 | 54 | 9242.99 | 176784.9627
1457-Induced draft fan lubrication systems | 46 | 46 | 11999.3 | 287033.8582
1460-Induced draft fan fouling | 19 | 19 | 2233.5 | 59839.8242
1470-Induced draft fan motors and drives | 277 | 277 | 24304.23 | 1828443.1039
1471-Induced draft fan motors - variable speed | 62 | 62 | 11092.23 | 254204.5454
1472-Inducted draft fan coupling | 16 | 16 | 2299.1 | 259575.6291
1475-Induced draft fan controls | 100 | 100 | 12084.03 | 126305.9848
1476-Induced draft fan speed changer | 28 | 28 | 4281.42 | 128328.6752
1480-Other induced draft fan problems | 195 | 195 | 21684.71 | 1199121.2735
1487-Air heater (tubular) | 6 | 6 | 990 | 24090.8995
1488-Air heater (regenerative) | 153 | 153 | 29690.86 | 1549492.4447
1489-Air heater (heat pipe; plate-type) | 4 | 5 | 738.14 | 84191.2087
1492-Air heater fouling (tubular) | 21 | 21 | 662.6 | 164862.2949
1493-Air heater fouling (regenerative) | 118 | 119 | 6171.9 | 652378.0253
1495-Other air heater fouling (heat pipe; plate-type) | 11 | 11 | 399 | 10518.3499
1500-Air heater soot blowers | 1 | 1 | 440 | 8990.6665
1510-Flue gas ducts (except recirculation) | 25 | 25 | 3287.19 | 605771.9559
1512-Flue gas expansion joints | 9 | 9 | 2987 | 303989.6494
1520-Flue gas dampers (except recirculation) | 7 | 7 | 3201 | 107144.0483
1530-Other flue gas problems | 48 | 49 | 3096.58 | 156990.4889
1535-Flue gas recirculating fan | 5 | 5 | 1947 | 7439.2158
1536-Flue gas recirculating fan dampers | 2 | 2 | 842 | 70687.8164
1550-Flue gas recirculation fan motors | 1 | 1 | 191 | 216.4666
1555-Flue gas recirculation fan controls | 1 | 1 | 705 | 1433.4998
1560-Other flue gas recirculation fan problems | 3 | 3 | 1180.2 | 3906.6129
1570-Flue gas recirculation ducts | 3 | 3 | 1415.13 | 725430.4883
1572-Flue gas recirculation duct expansion joints | 3 | 3 | 1850 | 107748.3328
1580-Flue gas recirculation dampers | 7 | 7 | 98 | 40236.4
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 21 | 22 | 4705.4 | 2002556.109
1591-Stack damper and linkage | 12 | 12 | 2593.4 | 12944.5521
1592-Stack damper linkage motors | 3 | 3 | 489 | 916.2997
1599-Other miscellaneous boiler air and gas system problems | 209 | 211 | 10334.27 | 388691.0396
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 151 | 152 | 46844.04 | 755865.8704
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 156 | 163 | 25597.18 | 283725.2511
1720-Desuperheater/attemperator controls | 53 | 53 | 11085.87 | 103805.2818
1730-Boiler explosion or implosion | 1 | 1 | 5 | 59.3333
1740-Boiler drum gage glasses/level indicator | 100 | 100 | 23513.37 | 234357.8883
1741-Furnace and water gauge television auxiliary system | 3 | 3 | 194 | 2435.6666
1750-Burner management system | 251 | 254 | 26940.4 | 206628.8028
1760-Feedwater instrumentation (not local controls) | 36 | 36 | 7339.32 | 77698.3672
1761-Combustion /Steam condition instrumentation (not local controls) | 21 | 21 | 7236.65 | 100579.3846
1762-Desuperheater/attemperator instrumentation (not local controls) | 6 | 6 | 842.28 | 1199.8956
1799-Other boiler instrumentation and control problems | 208 | 211 | 46040.29 | 428075.4936
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 58 | 58 | 2175.5 | 178540.9994
1810-Other boiler inspections | 7 | 7 | 405.74 | 22167.8185
1811-Boiler Inspections - problem identification/investigative | 1 | 1 | 243 | 22623.3
1812-Boiler Inspections - scheduled or routine | 5 | 5 | 477.83 | 5959.2265
1850-Boiler water condition (not feedwater water quality) | 357 | 357 | 52938.97 | 832785.9614
1900-Improper balance between tube sections not due to fouling or plugging | 2 | 2 | 335 | 173.8332
1910-Inadequate air not due to equipment problems | 88 | 88 | 2277.31 | 348191.0924
1980-Boiler safety valve test | 13 | 13 | 1260.69 | 20022.6896
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 62 | 65 | 18847 | 149647.5105
1999-Boiler; miscellaneous | 795 | 1159 | 27762.62 | 2325465.4678
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 3 | 3 | 315.68 | 31096.568
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 15 | 19 | 506.5 | 21693.6504
2035-Core xenon restrictions | 5 | 5 | 1153.3 | 224941.5332
2037-Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | 3 | 3 | 373.5 | 147504.7666
2060-Excore nuclear instrumentation | 3 | 3 | 44 | 167.3333
2070-Normal refueling | 4 | 4 | 3904.03 | 209741.6355
2090-Other core/fuel problems | 1 | 1 | 52.35 | 492.9625
2111-Control rod magnetic jack drives | 2 | 2 | 1843.4 | 71438.69
2112-Control rod hydraulic drives | 3 | 3 | 295.24 | 540.0795
2120-Control rod scram mechanisms | 1 | 1 | 1.57 | 1.7532
2152-Control rod drive power supplies | 1 | 1 | 348.76 | 12206.6
2160-Other control rod drive problems | 2 | 2 | 962 | 88264.15
2200-Reactor coolant/recirculating pumps | 2 | 2 | 698.11 | 27213.4109
2210-Reactor coolant/recirculating pump motors | 5 | 5 | 3453.99 | 1954912.2499
2220-Reactor coolant/recirculating pump MG sets | 2 | 2 | 65.02 | 277.322
2250-Reactor coolant system filters and strainers | 1 | 1 | 8.7 | 540.705
2290-Pressurizer spray valves | 1 | 1 | 877 | 21048
2300-Recirculation loop flow control valves | 4 | 4 | 198 | 11325.3332
2350-BWR feedwater controls | 1 | 1 | 445 | 35600
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 3 | 3 | 1264.5 | 132187.8246
2390-Other reactor coolant system instruments and controls | 3 | 3 | 1241.53 | 50416.2948
2399-Other miscellaneous reactor coolant system problems | 2 | 2 | 1369 | 134903.9623
2440-Steam generator chemistry (excluding feedwater chemistry) | 21 | 21 | 210.89 | 15388.2911
2460-Blowdown system valves B | 11 | 11 | 32.72 | 20925.3805
2500-Steam piping (up to turbine stop valves and bypass valves) | 1 | 1 | 908 | 48320.7327
2510-Main steam isolation valves (BWR and PWR) | 3 | 3 | 2513.53 | 163341.727
2521-Main steam safety/relief valve testing | 1 | 1 | 9 | 100.95
2530-Atmospheric or condenser dump valves (not SRVs) | 5 | 11 | 15 | 3724.8333
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 1 | 1 | 991.5 | 35710.5243
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 1 | 1 | 0 | 0
2650-Emergency diesel generators (including actuating systems) | 1 | 1 | 1218 | 158441.4996
2670-DC safety system power supplies | 1 | 1 | 817 | 37500.3
2720-Containment isolation valves and dampers | 1 | 1 | 481.87 | 17154.572
2770-Containment cooling system - normal | 1 | 1 | 991.5 | 318932.4993
2799-Other containment system problems | 4 | 4 | 2483.95 | 541417.4636
2816-Valves and piping | 1 | 1 | 1163 | 25237.1
2842-Auxiliary feedwater pump steam turbines (including steam control valves) | 1 | 1 | 66.93 | 39.0425
3110-Condenser tube leaks | 207 | 207 | 51921.69 | 2876575.2282
3111-Condenser tube fouling shell side | 11 | 11 | 942 | 118421.2662
3112-Condenser tube fouling tube side | 229 | 279 | 24159.12 | 425728.3006
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 161 | 166 | 14447.14 | 108977.9483
3116-Air-cooled condenser fans | 7 | 7 | 399 | 4863.8831
3118-Other Air-cooled condenser problems | 27 | 27 | 2538.5 | 24394.2327
3119-Other condenser tube casing or shell and internal problems | 4 | 4 | 372 | 38142.9833
3120-Tube sheets | 2 | 2 | 115 | 10088.3333
3121-Expansion joint | 3 | 3 | 741.9 | 85225.2712
3122-Gaskets and seals | 3 | 3 | 699 | 10421.6
3123-Hot well | 14 | 14 | 1793.7 | 180473.253
3124-Tube sheet fouling | 14 | 15 | 1481.1 | 70683.7497
3129-Other condenser casing or shell and internal problems | 32 | 32 | 3685.52 | 100224.4082
3130-Air ejectors | 11 | 11 | 1403.16 | 7735.6493
3131-Air ejector piping and valves | 13 | 13 | 2314.94 | 8886.1565
3132-Inter and after condensers | 4 | 4 | 289.9 | 1190.6499
3133-Vacuum pumps | 23 | 23 | 4402.09 | 55586.3671
3134-Vacuum pump piping and valves | 8 | 8 | 1186.61 | 2452.0295
3135-Vacuum pump motor and auxiliaries | 9 | 9 | 2864.7 | 22645.3489
3139-Other air extraction system problems - general | 15 | 15 | 1810.9 | 18924.234
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 157 | 157 | 29475.43 | 772416.0481
3150-Hot well level controls | 32 | 32 | 6787.59 | 31222.1419
3151-Vacuum pump and air ejector controls | 4 | 4 | 1129.13 | 4286.4103
3152-Air-cooled condenser controls | 4 | 4 | 286.56 | 198.0713
3159-Other condensing system controls and instruments | 13 | 13 | 3806.49 | 126536.2996
3186-Auxiliary Condenser and Associated Equipment | 18 | 18 | 1575.35 | 12691.1394
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 85 | 100 | 7115.32 | 448154.0049
3199-Other miscellaneous condensing system problems | 40 | 40 | 5233.07 | 225827.1495
3210-Circulating water pumps | 269 | 280 | 30460.7 | 1614670.7419
3211-Circulating water pump motors | 150 | 166 | 18248.84 | 1126888.9212
3220-Circulating water piping | 29 | 29 | 8702.33 | 1351084.3703
3221-Circulating water piping fouling | 27 | 40 | 572.62 | 1358.3933
3230-Circulating water valves | 41 | 41 | 6857.65 | 371413.4205
3231-Waterbox | 28 | 28 | 3878.91 | 148216.4321
3232-Condenser tube cleaning system including debris filter | 23 | 23 | 6983 | 32134.4977
3233-Circulating water priming system | 1 | 1 | 258 | 481.5998
3238-Cooling tower fan motors | 14 | 14 | 702.3 | 10222.5864
3239-Cooling tower fan motors - variable speed | 5 | 5 | 927 | 57968.7832
3240-Cooling tower fans | 108 | 110 | 4859.49 | 257792.9783
3241-Cooling tower efficiency below design | 11 | 11 | 215.65 | 4411.2541
3242-Cooling tower fill damage | 3 | 3 | 352.8 | 14626.5333
3243-Cooling tower icing | 1 | 1 | 27 | 989.1
3245-Other cooling tower problems | 66 | 66 | 6585.8 | 157542.114
3246-Cooling tower fouling | 2 | 2 | 60 | 1458
3247-Cooling tower instrumentation | 13 | 13 | 2608.28 | 9604.1024
3250-Circulating water system instruments and controls | 5 | 5 | 1169.3 | 29682.1711
3260-Traveling screens | 43 | 43 | 8317.65 | 552076.9831
3261-Traveling screen fouling | 8 | 9 | 2143.05 | 41773.9295
3269-Circulating water biological conditions (ie; zebra mussels) | 19 | 21 | 4268.72 | 56992.2413
3270-Intake system problems other than traveling screens | 16 | 16 | 3057.28 | 66927.6747
3271-Intake grating fouling | 5 | 5 | 964 | 3774.4166
3272-Circulating water screenwash system | 5 | 5 | 916 | 84941.2662
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 46 | 46 | 3913.93 | 95837.2222
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 2 | 2 | 490 | 3425.9163
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 82 | 82 | 9116.95 | 77543.3403
3281-Circulating water tempering system | 1 | 1 | 15 | 127.5
3282-Circulating water cooling ponds | 1 | 1 | 150 | 11597.4999
3285-Circulating water chemistry | 9 | 9 | 2360 | 97995.3826
3290-Waste water (zero discharge) tanks; pumps and motors | 3 | 3 | 643 | 2914.0831
3292-Waste water (zero discharge) piping | 2 | 2 | 352 | 22717.2666
3295-Other Waste water (zero discharge) problems | 3 | 3 | 404 | 16783.1665
3299-Other circulating water system problems | 61 | 61 | 9358.8 | 243993.2304
3300-Condensate water pre-treatment | 11 | 11 | 1614.77 | 44285.4951
3310-Condensate/hotwell pumps | 96 | 96 | 14394.65 | 639853.3793
3311-Condensate/hotwell pump motor | 53 | 53 | 7602.52 | 455190.5566
3312-Condensate booster pump | 11 | 11 | 4221.44 | 80412.2333
3313-Condensate booster pump motor | 3 | 3 | 173.7 | 2820.9016
3314-Condensate booster pump motor - variable speed | 4 | 4 | 801 | 2229.6499
3315-Condensate booster pump drive (other than 3313 and 3314) | 11 | 11 | 1723 | 9693.2322
3320-Condensate piping | 19 | 19 | 6141.93 | 169272.5319
3330-Condensate valves | 47 | 47 | 12689.34 | 385875.9925
3339-LP heater head leaks | 1 | 1 | 45 | 17.25
3340-LP heater tube leaks | 12 | 12 | 2903.14 | 285430.4067
3341-Other LP heater - general | 15 | 15 | 3115.5 | 92917.5069
3342-IP heater tube leaks | 8 | 8 | 2652.16 | 75073.9444
3343-Other IP heater - general | 11 | 11 | 2218.2 | 70807.5492
3344-Deaerator (including level control) | 47 | 47 | 9098.45 | 104360.3914
3345-IP heater head leaks | 3 | 3 | 445 | 446.9666
3350-Condensate polishing and filtering systems | 50 | 50 | 5911.16 | 89642.4131
3351-Chemical addition systems | 3 | 3 | 347 | 1212.9665
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 113 | 113 | 19186.42 | 729075.2956
3360-Condensate makeup and return (including storage tanks) | 37 | 37 | 4683.33 | 149544.5839
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 24 | 24 | 6079.7 | 41555.0514
3380-Condensate coolers | 3 | 3 | 685.85 | 44310.4864
3399-Other miscellaneous condensate system problems | 56 | 56 | 8501.41 | 369403.9582
3401-Startup feedwater pump | 21 | 21 | 6175.48 | 660476.6146
3402-Startup feedwater pump drives - all types | 3 | 3 | 2241 | 60880.4993
3407-Feedwater pump suction screens | 13 | 13 | 2789.22 | 30213.2234
3408-Feedwater pump drive - local controls | 28 | 28 | 8328.76 | 61783.2075
3409-Feedwater pump drive motor - variable speed | 13 | 13 | 1351.3 | 299003.2381
3410-Feedwater pump | 384 | 384 | 83018.24 | 4036779.4129
3411-Feedwater pump drive - motor | 77 | 77 | 10356.57 | 918931.9407
3412-Feedwater pump drive - steam turbine | 114 | 114 | 30202.41 | 1804729.849
3413-Feedwater pump coupling and drive shaft | 29 | 29 | 4359.04 | 722428.6655
3414-Feedwater pump local controls | 43 | 43 | 14282.88 | 236210.5509
3415-Feedwater pump/drive lube oil system | 115 | 115 | 25599.93 | 593445.4017
3416-Other feedwater pump problems | 429 | 611 | 29110.61 | 903445.4498
3417-Feedwater pump drive - main shaft | 3 | 3 | 394 | 42472.2165
3418-Feedwater pump drive - other | 10 | 10 | 2619 | 26251.8492
3419-Feedwater pump drive - gear | 7 | 7 | 2027 | 65373.1496
3420-Feedwater piping and supports | 32 | 32 | 8314.96 | 1599578.6697
3430-Feedwater regulating (boiler level control) valve | 138 | 138 | 30028.92 | 2010199.9424
3431-Other feedwater valves | 126 | 126 | 33595.77 | 580282.2867
3439-HP heater head leaks | 11 | 11 | 2468.49 | 57870.1434
3440-High pressure heater tube leaks | 220 | 222 | 14556.13 | 690946.6759
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 55 | 55 | 12886.02 | 305642.8882
3452-Feedwater Booster Pump Drive - Local Controls | 1 | 1 | 148.7 | 4195.8182
3454-Feedwater Booster Pump | 14 | 14 | 2726.1 | 59570.1141
3455-Feedwater Booster Pump Drive - Motor | 3 | 3 | 697 | 14769.4498
3456-Feedwater Booster Pump Drive - Steam Turbine | 1 | 1 | 487 | 2702.85
3457-Feedwater Booster Pump Coupling and Drive Shaft | 1 | 1 | 103 | 1417.9666
3458-Feedwater Booster Pump Local Controls | 15 | 15 | 719.1 | 73686.1649
3460-Other Feedwater Booster Pump Problems | 3 | 3 | 405 | 2662.3998
3499-Other feedwater system problems | 139 | 139 | 21046.1 | 636396.1995
3501-Heater drain pumps | 28 | 28 | 4439.4 | 171763.0567
3502-Heater level control | 27 | 27 | 4705.9 | 148634.1897
3503-Heater drain piping | 17 | 17 | 3103.18 | 62035.5374
3504-Heater drain valves | 22 | 22 | 1634.54 | 68501.5073
3505-Heater drain pump drive | 1 | 1 | 72 | 47128.8
3509-Other heater drain system problems | 10 | 10 | 1045.44 | 20524.9453
3520-HP Extraction steam piping | 10 | 10 | 1927.36 | 67942.42
3521-HP Extraction steam valves | 7 | 7 | 795.04 | 44306.458
3522-HP Extraction steam instruments and controls | 5 | 5 | 688.3 | 2846.8979
3529-Other HP extraction steam system problems | 2 | 2 | 197 | 8438.5999
3530-IP Extraction steam piping | 3 | 3 | 1238 | 137385.4994
3531-IP Extraction steam valves | 11 | 11 | 1975.38 | 45942.4844
3539-Other IP extraction steam system problems | 18 | 18 | 933 | 61776.933
3541-LP Extraction steam valves | 13 | 13 | 3097 | 209025.0153
3542-LP Extraction steam instruments and controls | 1 | 1 | 0 | 0
3549-Other LP extraction steam system problems | 1 | 1 | 45 | 465
3600-Switchyard transformers and associated cooling systems - external | 61 | 61 | 3575.42 | 186145.6762
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 9 | 9 | 814.84 | 121162.3913
3610-Switchyard circuit breakers - (not outside management control) | 60 | 60 | 12147.01 | 595657.1797
3611-Switchyard circuit breakers - external | 132 | 132 | 20862.74 | 575275.8211
3612-Switchyard system protection devices - external | 137 | 137 | 19034.18 | 503268.8142
3613-Switchyard system protection devices - (not outside management control) | 39 | 39 | 6084.86 | 822716.9822
3618-Other switchyard equipment ? (not outside management control) | 25 | 25 | 4698.98 | 210934.0373
3619-Other switchyard equipment - external | 101 | 101 | 10552.81 | 538014.7099
3620-Main transformer | 381 | 388 | 51779.34 | 8710893.0121
3621-Unit auxiliaries transformer | 146 | 146 | 28230.11 | 1364620.7294
3622-Station service startup transformer | 31 | 31 | 9410.6 | 423334.8703
3623-Auxiliary generators | 2 | 2 | 357.74 | 474.0055
3624-Generator Voltage Supply System | 12 | 12 | 1024.9 | 9251.7214
3629-Other switchyard or high voltage system problems - external | 123 | 124 | 20382.89 | 1040469.525
3630-480-volt transformers | 15 | 15 | 3204.4 | 249531.5528
3631-480-volt circuit breakers | 70 | 70 | 11785.14 | 145200.5744
3632-480-volt conductors and buses | 40 | 40 | 5031.01 | 784114.7964
3634-480-volt protection devices | 21 | 21 | 2550.9 | 20406.3157
3639-Other 480-volt problems | 31 | 31 | 4597.07 | 58132.7271
3640-AC instrument power transformers | 16 | 16 | 2084.6 | 43128.2625
3641-AC Circuit breakers | 85 | 85 | 15567.6 | 305656.6488
3642-AC Conductors and buses | 41 | 41 | 6698.32 | 515833.3441
3643-AC Inverters | 30 | 30 | 8373.29 | 79685.4325
3644-AC Protection devices | 112 | 112 | 12739.16 | 311404.611
3649-Other AC instrument power problems | 20 | 20 | 2952.4 | 14353.1777
3650-DC instrument power battery chargers | 28 | 28 | 4733.04 | 348008.3997
3651-DC circuit breakers | 16 | 16 | 1306.25 | 62841.3363
3652-DC conductors and buses | 4 | 4 | 1992.1 | 153415.1338
3653-DC protection devices | 17 | 17 | 1720.95 | 65173.4596
3659-Other DC power problems | 50 | 50 | 6292.15 | 97115.4261
3660-4160-volt transformers | 39 | 39 | 9981 | 384222.3627
3661-4160-volt circuit breakers | 93 | 94 | 21559.28 | 563551.2048
3662-4160-volt conductors and buses | 17 | 17 | 4426.61 | 776227.9941
3664-4160-volt protection devices | 34 | 34 | 4535.93 | 128943.8198
3669-Other 4160-volt problems | 8 | 8 | 1031 | 8755.2998
3670-12kV transformers | 11 | 11 | 1070.34 | 29116.1776
3671-12kV circuit breakers | 54 | 54 | 3955.27 | 169659.0579
3672-12kV conductors and buses | 40 | 40 | 6686.32 | 1084563.7192
3673-12kV insulators | 3 | 3 | 134.14 | 1116.3903
3674-12kV protection devices | 53 | 53 | 5040.68 | 222524.5898
3679-Other 12kV problems | 11 | 11 | 1426.99 | 745.7529
3680-Other voltage system transformers | 20 | 20 | 2422.62 | 118480.3985
3681-Other voltage system breakers | 48 | 48 | 7358.99 | 430176.9943
3682-Other voltage system conductors and buses | 34 | 34 | 5029.03 | 235867.0423
3683-Other voltage system insulators | 13 | 13 | 1869 | 166092.3746
3684-Other voltage system protection devices | 33 | 33 | 5610.21 | 96256.7083
3689-Other Other voltage system problems | 46 | 46 | 6861.77 | 494726.1564
3690-Station Service Power Distribution System; General | 62 | 62 | 8155.53 | 554025.7078
3700-Power Station switchyard (non generating unit equipment) | 26 | 26 | 2892.99 | 125144.3932
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 105 | 105 | 14096.73 | 557715.4388
3720-Transmission equipment at the 1st substation) | 33 | 33 | 5223.1 | 83146.9381
3730-Transmission equipment beyond the 1st substation | 64 | 64 | 8002.62 | 174498.811
3800-Open cooling water pumps and motors | 10 | 10 | 2660 | 59291.7656
3801-Open cooling water piping | 4 | 4 | 784 | 44546.8997
3802-Open cooling water valves | 7 | 7 | 757 | 19633.0664
3803-Open cooling water heat exchangers | 1 | 1 | 246.3 | 2963.8099
3804-Open cooling water system fouling | 2 | 2 | 796 | 8965.7328
3806-Open cooling water strainer | 1 | 1 | 415 | 10879.9164
3810-Service water pumps and motors | 15 | 15 | 1334.65 | 8764.1368
3811-Service water piping | 31 | 31 | 6519.6 | 555398.0241
3812-Service water valves | 7 | 7 | 446.23 | 35677.3897
3813-Service water heat exchangers | 6 | 6 | 295.11 | 26934.8082
3814-Service water system fouling | 6 | 6 | 2423.97 | 123432.2918
3815-Service water strainer | 1 | 1 | 240.7 | 1307.8033
3819-Other service water problems A | 29 | 29 | 4079.98 | 361072.1107
3820-Closed cooling water pumps | 16 | 16 | 2950.73 | 30973.2716
3821-Closed cooling water piping | 17 | 17 | 1719.1 | 98991.8677
3822-Closed cooling water valves | 25 | 25 | 2507.42 | 55993.788
3823-Closed cooling water heat exchangers | 24 | 24 | 3764.1 | 135796.1788
3824-Closed cooling water system fouling | 12 | 12 | 2088.7 | 63384.3093
3825-Closed cooling water instrumentation | 1 | 1 | 489 | 3088.8497
3826-Closed cooling water strainer | 1 | 1 | 175 | 1239.5833
3829-Other closed cooling water system problems A | 49 | 49 | 6596.91 | 54121.4537
3830-Auxiliary boiler | 41 | 41 | 10130.02 | 269813.7304
3831-Auxiliary steam piping | 5 | 5 | 1418.27 | 39737.9154
3832-Auxiliary steam valves | 27 | 27 | 6911.13 | 154047.794
3833-Auxiliary steam controls and instruments | 16 | 16 | 4115.5 | 94936.2577
3834-Auxiliary boiler tube leaks | 13 | 13 | 2205.5 | 318946.9245
3835-Auxiliary boiler burner management system | 1 | 1 | 752 | 23312
3836-Steam Transfer to Other Unit | 99 | 100 | 7873.81 | 295416.2452
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 22 | 23 | 2552.03 | 168999.4656
3840-Service air compressors | 20 | 20 | 3155.62 | 145912.6219
3841-Service air piping | 10 | 10 | 3700.28 | 5089.2363
3842-Service air valves | 1 | 1 | 17 | 17
3843-Service air dryers | 1 | 1 | 251 | 62.75
3844-Soot blowing air compressor and system | 3 | 3 | 1092 | 86657.9995
3849-Other service air problems | 9 | 9 | 798 | 14035.0164
3850-Instrument air compressors | 70 | 70 | 6239.65 | 126992.547
3851-Instrument air piping | 17 | 17 | 3828.74 | 80639.2738
3852-Instrument air valves | 8 | 8 | 747.53 | 1082.3027
3853-Instrument air dryers | 8 | 8 | 1461 | 24925.2664
3859-Other instrument air problems | 30 | 30 | 3913.78 | 21711.6807
3860-Fire protection system pumps | 5 | 5 | 634.9 | 78448.0597
3861-Fire protection system piping | 21 | 21 | 3529.52 | 69369.3482
3862-Fire protection system valves | 7 | 7 | 1081 | 20210.733
3863-Fire protection system fouling | 1 | 1 | 40 | 1970
3864-Fire protection system instrumentation and controls | 93 | 93 | 8913.69 | 200224.062
3869-Other fire protection system problems | 45 | 45 | 3534.16 | 294528.4629
3870-Fuel Gas Compressor and Motors | 47 | 47 | 2204.77 | 173758.4852
3871-Fuel Gas Compressor Piping | 22 | 22 | 1277.2 | 21635.1497
3872-Fuel Gas Compressor Valves | 39 | 39 | 4546.58 | 87772.5871
3873-Fuel Gas Compressor Heat Exchangers | 14 | 14 | 2017.1 | 15950.4461
3874-Fuel Gas Compressor Controls and Instrumentation | 65 | 66 | 6271.7 | 20612.421
3875-Fuel Gas Compressor Filters | 1 | 1 | 48 | 208.8
3879-Fuel Gas Compressor - other | 70 | 70 | 4214.52 | 13782.6706
3880-Seal air fan | 1 | 1 | 98 | 1568
3881-Seal air fan drive - motor | 1 | 1 | 335 | 195.4166
3889-Other seal air fan system problems | 1 | 1 | 590 | 11013.3329
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 102 | 105 | 6114.92 | 92324.7261
3899-Other miscellaneous auxiliary system problems | 133 | 133 | 12022.88 | 195347.9051
3950-Process computer | 65 | 65 | 7279.03 | 114975.0861
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 137 | 139 | 5286.96 | 1488995.6201
3970-Distributive Control System (DCS) - process computer | 88 | 101 | 12536.68 | 1678743.8127
3971-DCS - data highway | 38 | 38 | 4861.2 | 41520.7333
3972-DCS - hardware problems (including card failure) | 166 | 167 | 22805.69 | 175660.9711
3973-DCS - internal and termination wiring | 19 | 19 | 1943.3 | 35917.6025
3974-DCS - logic problems | 64 | 65 | 9323.31 | 79497.6355
3975-DCS - upgrades | 36 | 36 | 5758.45 | 28721.4514
3979-Other DCS problems | 65 | 65 | 9664.93 | 487992.8254
3980-Programmable Logic Controller (PLC) | 30 | 30 | 3661.8 | 22588.1074
3981-PLC - data highway | 40 | 40 | 1215 | 5180.8747
3982-PLC - hardware problems (including card failure) | 41 | 41 | 4836.65 | 336945.152
3983-PLC - internal and termination wiring | 5 | 5 | 112 | 163.4166
3984-PLC - logic problems | 15 | 15 | 736.16 | 30544.9778
3985-PLC - upgrades | 11 | 11 | 826.3 | 6723.064
3989-Other PLC problems | 24 | 24 | 1938.95 | 36066.2393
3995-Powerhouse heating and ventilating systems | 7 | 7 | 420.42 | 6889.6375
3996-Air conditioning systems - rooms and areas | 7 | 7 | 983.4 | 1687.3596
3998-Balance of plant overhaul/outage | 24 | 24 | 3266.11 | 199424.686
3999-Other miscellaneous balance of plant problems | 580 | 594 | 59265.96 | 1523957.138
4000-Outer casing A | 10 | 10 | 2837.6 | 296516.5828
4001-Inner casing C | 6 | 6 | 989 | 10339.5661
4009-Nozzle bolting A | 2 | 2 | 47 | 925.3667
4010-Nozzles and nozzle blocks C | 3 | 3 | 150.94 | 37714.8403
4011-Diaphragms A | 3 | 3 | 193 | 87570.0166
4012-Buckets or blades A | 6 | 6 | 1925 | 1604550.0496
4014-Bucket or blade fouling C | 375 | 599 | 3885 | 216770.1654
4020-Shaft seals B | 13 | 13 | 2526.46 | 10524.841
4030-Rotor shaft C | 5 | 5 | 1580.22 | 58986.8534
4040-Bearings C | 69 | 73 | 15310.07 | 4985582.1717
4041-HP steam turbine thrust bearings | 6 | 6 | 728.3 | 35050.675
4099-Other high pressure turbine problems | 81 | 81 | 28950.8 | 953161.4863
4100-Outer casing B | 6 | 6 | 1038 | 16787.0329
4101-Inner casing B | 3 | 3 | 478 | 255612
4112-Buckets or blades B | 2 | 2 | 1593 | 2712513.9824
4113-Bucket or blade fouling B | 9 | 9 | 122 | 26917.35
4120-Shaft seals C | 3 | 3 | 998 | 311883.3994
4130-Rotor shaft B | 2 | 2 | 603.69 | 6395.4888
4140-Bearings D | 14 | 14 | 4676.02 | 406631.1691
4141-IP steam turbine thrust bearings | 4 | 4 | 308 | 7486.9666
4199-Other intermediate pressure turbine problems | 11 | 11 | 2439.73 | 80148.2723
4211-Diaphragms C | 1 | 1 | 258 | 2416.5998
4212-Buckets or blades C | 12 | 12 | 1735.9 | 600380.5565
4215-Wheels or spindles B | 1 | 1 | 158 | 123872
4220-Shaft seals D | 8 | 8 | 1476.38 | 207853.8515
4230-Rotor shaft A | 4 | 4 | 1337 | 654613.4997
4240-Bearings E | 36 | 36 | 8898.8 | 996331.309
4241-LP steam turbine thrust bearings | 1 | 1 | 76 | 267.2666
4250-Other low pressure turbine problems | 27 | 27 | 8889.19 | 310460.1075
4260-Main stop valves | 116 | 116 | 23870.37 | 980105.2476
4261-Control valves | 309 | 310 | 59192.86 | 2650147.9808
4262-Intercept valves | 50 | 50 | 12982.43 | 221490.8626
4263-Reheat stop valves | 34 | 34 | 11633.56 | 202183.9818
4264-Combined intercept valves | 8 | 8 | 2102.48 | 19937.7543
4265-Miscellaneous drain and vent valves | 24 | 24 | 6048.48 | 301831.1376
4266-Main stop valve testing | 5 | 5 | 1075.62 | 2396.8191
4267-Control valve testing | 25 | 25 | 7644.82 | 15023.1642
4268-Reheat/intercept valve testing | 12 | 12 | 2239.46 | 11481.6224
4269-Other turbine valves (including LP steam admission valves) | 87 | 87 | 15709.7 | 708826.8029
4270-Crossover or under piping | 22 | 22 | 9638.3 | 764498.2219
4279-Miscellaneous turbine piping | 34 | 34 | 10282.35 | 550305.0057
4280-Lube oil pumps A | 23 | 23 | 7152.18 | 884289.9988
4281-Lube oil coolers A | 13 | 13 | 4277.49 | 132597.5803
4282-Lube oil conditioners | 1 | 1 | 117 | 239.85
4283-Lube oil system valves and piping | 19 | 20 | 3851.02 | 286582.2647
4284-Lube oil pump drive | 7 | 7 | 1960 | 699339.9393
4289-Other lube oil system problems | 67 | 67 | 12539.27 | 972069.9419
4290-Hydraulic system pumps | 31 | 31 | 7051.22 | 106167.0338
4291-Hydraulic system coolers | 4 | 4 | 782 | 4154.733
4292-Hydraulic system filters | 14 | 14 | 4129.89 | 78704.1385
4293-Hydraulic system pipes and valves | 84 | 84 | 23575.59 | 748507.0485
4299-Other hydraulic system problems | 67 | 67 | 14425.64 | 221710.6246
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 30 | 30 | 6664.38 | 165756.3219
4301-Turbine governing system | 69 | 69 | 12176.89 | 441025.7523
4302-Turbine trip devices (including instruments) | 164 | 164 | 38693.79 | 380717.6926
4303-Exhaust hood and spray controls | 15 | 15 | 3266.9 | 37017.2544
4304-Automatic turbine control systems - mechanical | 5 | 5 | 794.89 | 10904.2532
4305-Automatic turbine control systems - mechanical - hydraulic | 25 | 25 | 5052.31 | 112893.9357
4306-Automatic turbine control systems - electro-hydraulic - analog | 10 | 10 | 2327.44 | 11840.5662
4307-Automatic turbine control systems - electro-hydraulic - digital | 17 | 17 | 4253.21 | 85245.4419
4308-Automatic turbine control systems - digital control and monitoring | 45 | 45 | 10529.09 | 135858.7966
4309-Other turbine instrument and control problems | 144 | 144 | 25994.63 | 576737.7645
4310-Steam Turbine Control System - data highway | 13 | 13 | 2640.38 | 37848.1709
4311-Steam Turbine Control System - hardware problems (including card failure) | 57 | 57 | 11403.76 | 126745.5541
4312-Steam Turbine Control System - internal and termination wiring | 14 | 14 | 3751.3 | 13942.6872
4313-Steam Turbine Control System - logic problems | 38 | 40 | 7434.19 | 24529.2284
4314-Steam Turbine Control System - upgrades | 13 | 13 | 2218 | 45346.2162
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 12 | 12 | 1855.16 | 499785.9734
4401-Inspection F | 1 | 1 | 138 | 238257
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 7 | 7 | 1302.4 | 144375.2511
4410-Turning gear and motor A | 37 | 37 | 8661.56 | 310085.3594
4411-Steam turbine gear box (single shaft configuration) | 1 | 1 | 20 | 95040
4412-Steam turbine clutch (single shaft configuration) | 1 | 1 | 480 | 9663.9998
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 263 | 266 | 61516.38 | 2632257.2292
4430-Gland seal system | 52 | 52 | 12934 | 363407.9401
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 11 | 11 | 2392.58 | 24758.9138
4445-Steam reheater | 1 | 1 | 9 | 22.8
4450-Water induction | 7 | 7 | 653.84 | 1082.0191
4460-Turbine overspeed trip test | 7 | 7 | 4050 | 284691.8158
4470-Differential expansion | 60 | 60 | 13429.45 | 1412207.8364
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 6 | 6 | 1099.69 | 17772.4236
4499-Other miscellaneous steam turbine problems | 253 | 254 | 48419.76 | 1668558.6184
4500-Rotor windings (including damper windings and fan blades on hydro units) | 66 | 66 | 11133.17 | 7031098.3717
4510-Rotor collector rings | 18 | 18 | 3438.4 | 390208.0371
4511-Rotor; General | 44 | 44 | 3767.46 | 1000478.8368
4520-Stator windings; bushings; and terminals | 81 | 82 | 11783.72 | 6014218.7509
4530-Stator core iron | 5 | 5 | 707.76 | 474374.2405
4535-Stator; General | 47 | 47 | 7937.05 | 1218641.9765
4536-Generator heaters | 3 | 3 | 150 | 1646.25
4540-Brushes and brush rigging | 19 | 19 | 3224.05 | 515811.9464
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 87 | 87 | 4974.75 | 1327319.1107
4551-Generator bearings | 104 | 104 | 18494.74 | 2509951.3765
4552-Generator lube oil system | 97 | 102 | 5766.03 | 266818.1453
4555-Bearing cooling system A | 44 | 44 | 2548.52 | 291118.0921
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 130 | 131 | 11104.72 | 794992.9286
4570-Generator casing | 2 | 2 | 94.96 | 7843.7333
4590-Generator brakes | 28 | 28 | 2479.6 | 29619.218
4600-Exciter drive - motor | 21 | 21 | 3065.09 | 476603.1544
4601-Exciter field rheostat | 12 | 12 | 2082.9 | 124286.9844
4602-Exciter commutator and brushes | 51 | 51 | 11592.81 | 2513416.9923
4603-Solid state exciter element | 56 | 57 | 10431.05 | 147390.7701
4604-Exciter drive - shaft | 5 | 5 | 441 | 15989.3833
4605-Exciter transformer | 21 | 21 | 3423.95 | 133956.8565
4609-Other exciter problems | 511 | 513 | 85111.39 | 3994775.1073
4610-Hydrogen cooling system piping and valves | 34 | 34 | 8426.31 | 609231.2412
4611-Hydrogen coolers | 63 | 63 | 10124.23 | 619863.9886
4612-Hydrogen storage system | 4 | 4 | 1417 | 35417.9664
4613-Hydrogen seals | 15 | 15 | 4675.5 | 654529.7152
4619-Other hydrogen system problems | 29 | 29 | 5096.89 | 378290.7129
4620-Air cooling system | 44 | 44 | 4039.64 | 62924.99
4630-Liquid cooling system | 64 | 64 | 12983.74 | 187763.8975
4640-Seal oil system and seals A | 32 | 32 | 8467.38 | 791455.4088
4650-Other cooling system problems | 100 | 100 | 9139.89 | 213615.7892
4700-Generator voltage control | 204 | 204 | 33116.58 | 821146.3936
4710-Generator metering devices | 75 | 75 | 7068.75 | 188437.61
4720-Generator synchronization equipment | 146 | 149 | 16789.58 | 229368.9855
4730-Generator current and potential transformers | 139 | 139 | 20449.61 | 509376.0608
4740-Emergency generator trip devices | 260 | 309 | 33345.5 | 1468093.3825
4750-Other generator controls and metering problems | 264 | 268 | 29970.27 | 1700382.7547
4800-Generator main leads | 21 | 21 | 4524.22 | 547651.3682
4805-Generator Bus Duct Cooling System | 50 | 50 | 6549.16 | 126972.7898
4810-Generator output breaker | 359 | 365 | 36152.77 | 2806615.5721
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 27 | 29 | 3306.58 | 2323633.2241
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 2 | 2 | 103 | 6471.9999
4840-Inspection E | 47 | 47 | 2235.06 | 353543.8068
4841-Generator doble testing | 3 | 3 | 432.13 | 567.0904
4842-Reactive and capability testing | 7 | 7 | 706.62 | 1379.8726
4850-Core monitor alarm | 4 | 4 | 857 | 912487.0998
4860-Generator Neutral Grounding Equipment | 30 | 30 | 7189.64 | 599417.0209
4899-Other miscellaneous generator problems | 236 | 236 | 30078.77 | 2917923.9195
5000-Inlet air ducts A | 12 | 12 | 1060.64 | 148001.0593
5001-Inlet air vanes / nozzles | 144 | 146 | 17738.43 | 457665.0422
5002-Inlet air filters A | 184 | 186 | 10718.88 | 166280.7319
5004-Inlet air chillers B | 37 | 37 | 1128.94 | 130690.8415
5005-Inlet air evaporative coolers B | 44 | 44 | 2609.96 | 2012908.8486
5006-Inlet air foggers B | 15 | 15 | 122.42 | 4049.1716
5009-Other inlet air problems A | 64 | 64 | 5365.71 | 447216.0718
5010-High pressure shaft D | 4 | 4 | 436 | 44348.8999
5011-High pressure bearings C | 2 | 2 | 147.7 | 334.9366
5012-High pressure blades/buckets B | 18 | 18 | 3255.73 | 1081353.9619
5013-Compressor casing and bolts | 12 | 12 | 1420.5 | 173252.7415
5014-Compressor diaphragms | 10 | 10 | 1328.44 | 6842.687
5015-Compressor seals | 2 | 2 | 115 | 778.6666
5016-High pressure compressor bleed valves | 195 | 199 | 28862.81 | 227656.4239
5017-Low pressure compressor bleed valves | 68 | 68 | 9086.24 | 79053.6381
5019-Other high pressure problems A | 14 | 14 | 1436 | 95624.7161
5022-Low pressure blades/buckets A | 4 | 4 | 1437.3 | 805.133
5029-Other low pressure problems E | 17 | 17 | 908.69 | 9549.9449
5030-Supercharging fans A | 1 | 1 | 17 | 112151.8333
5035-Compressor Washing | 17 | 17 | 882.6 | 43955.654
5036-Compressor shaft & bearings two sft machines | 3 | 3 | 323.73 | 1889.8682
5037-Inlet bleed heat valve | 58 | 58 | 8007.21 | 69144.4977
5039-Other compressor problems | 108 | 112 | 12200.67 | 1045819.2933
5041-Fuel piping and valves A | 744 | 753 | 99559.97 | 2247526.3294
5042-Fuel nozzles/vanes B | 66 | 66 | 8688.29 | 309696.5419
5043-Fuel filters A | 74 | 77 | 11089.56 | 177176.2781
5044-Liquid fuel oil pump A | 14 | 14 | 1867.29 | 17931.2597
5046-Liquid fuel oil transfer/forwarding pump B | 19 | 19 | 2989.19 | 5485.6044
5047-Liquid fuel purge system A | 20 | 42 | 3032.54 | 11615.0056
5048-Gas fuel system B | 660 | 669 | 85533.82 | 912549.864
5049-Other fuel system problems B | 310 | 315 | 36676.83 | 845331.4783
5050-Ignition system A | 282 | 285 | 39554.97 | 313714.5473
5051-Pilot fuel piping and valves A | 77 | 77 | 11878.27 | 88708.7126
5052-Pilot fuel nozzles/vanes B | 4 | 4 | 600 | 12158.7466
5053-Pilot fuel filters A | 3 | 3 | 766 | 4632.7996
5054-Water Injection System (Gas Turbine) | 134 | 136 | 8987.13 | 127835.3635
5060-Atomizing air system B | 34 | 34 | 3479.56 | 162776.4284
5065-NOx water injection system including pumps | 102 | 102 | 6655.65 | 107395.7699
5066-NOx Steam Injection System | 16 | 16 | 1128.18 | 3451.6126
5070-Combustor casing A | 21 | 21 | 5945.87 | 120374.5107
5071-Combustor liner B | 6 | 6 | 1246.5 | 48635.5998
5072-Combustor caps B | 4 | 4 | 419 | 13686.7667
5073-Flame scanners B | 123 | 124 | 15430.89 | 135952.2016
5074-Flashback including instruments | 88 | 90 | 12013.95 | 184189.1075
5075-Blade Path Temperature Spread A | 240 | 241 | 42260.31 | 807192.1593
5079-Other combustor problems B | 361 | 366 | 51933.82 | 1399575.8728
5080-High pressure shaft C | 13 | 13 | 1618 | 225966.6827
5081-High pressure bearings D | 88 | 128 | 6286.63 | 327079.0711
5082-High pressure blades/buckets A | 20 | 20 | 2945.84 | 992222.5185
5083-High pressure nozzles/vanes A | 5 | 5 | 521 | 279136.2933
5084-High pressure casing/expansion joints | 3 | 5 | 178.04 | 5343.8006
5085-Interstage gas passages - HP | 4 | 4 | 263.2 | 3868.1215
5086-High pressure shaft seals A | 5 | 5 | 233 | 123500.0166
5087-Thrust Bearing | 8 | 8 | 813.44 | 4950.8979
5088-Gas turbine cooling steam | 38 | 38 | 7002.39 | 116689.1963
5089-Other high pressure problems B | 20 | 23 | 1342.5 | 3563.4329
5090-Low pressure shaft A | 2 | 2 | 55 | 1540
5091-Low pressure bearings A | 9 | 9 | 1242.63 | 86223.4662
5092-Low pressure blades/buckets D | 19 | 19 | 2620.4 | 688005.9991
5093-Low pressure nozzles/vanes B | 2 | 2 | 93 | 9125
5094-Low pressure casing/expansion joints A | 3 | 3 | 812.01 | 32281.5753
5096-Low pressure shaft seals | 2 | 2 | 140 | 78302.3332
5097-Other low pressure problems B | 6 | 6 | 361.59 | 264886.5642
5098-Expansion joints A | 14 | 14 | 2885 | 246611.4657
5099-HP to LP coupling | 1 | 1 | 35 | 254.9167
5100-Chamber A | 6 | 6 | 767.14 | 34835.0516
5101-Hoods B | 1 | 1 | 23 | 32.9667
5102-Vanes/nozzles A | 4 | 4 | 553.8 | 120813.7831
5103-Silencer B | 1 | 1 | 168 | 28224
5104-Cones A | 4 | 4 | 641 | 58405.9329
5105-Diverter Dampers B | 18 | 18 | 2082.39 | 18374.7869
5106-Exhaust Stack | 11 | 11 | 1665.31 | 107624.0606
5108-High engine exhaust temperature A | 95 | 95 | 12026.77 | 160425.7908
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 175 | 175 | 23752.57 | 355732.61
5110-Lube oil system - general | 260 | 265 | 19306.17 | 1122008.0715
5111-Lube oil pumps B | 80 | 80 | 8153.99 | 128972.1756
5112-Lube oil coolers B | 17 | 17 | 2091.1 | 32476.3151
5113-Lube oil valves/piping | 45 | 45 | 3336.4 | 232504.1223
5114-Lube oil filters | 17 | 17 | 1307 | 6245.6164
5115-Oil vapor extractor | 16 | 16 | 891.5 | 5208.0496
5116-Power Augmentation System Equipment B | 11 | 11 | 209.17 | 76489.1144
5117-Power augmentation piping | 4 | 4 | 157.2 | 1361.1033
5118-Power augmentation valves | 11 | 11 | 825.12 | 2072.0654
5119-Power augmentation controls | 5 | 5 | 108.55 | 20784.8958
5120-Hydraulic oil system A | 126 | 126 | 13115.78 | 238565.0712
5121-Hydraulic oil system pumps | 16 | 16 | 1594.92 | 102912.1419
5122-Hydraulic oil system piping/valves | 35 | 35 | 4033.43 | 27817.6919
5130-Starting system (including motor) A | 383 | 384 | 49791.36 | 1987939.2633
5140-Battery and charger system B | 9 | 9 | 793.02 | 6725.3705
5150-Turning gear and motor C | 57 | 57 | 5607.3 | 449014.3736
5151-Load gear compartment B | 3 | 3 | 206 | 602.7999
5160-Cooling and seal air system B | 151 | 151 | 25812.97 | 279374.638
5170-Cooling water system A | 36 | 36 | 4836.83 | 90647.8711
5180-Anti-icing system A | 19 | 19 | 2964.58 | 19363.0936
5190-Other auxiliary system problems A | 157 | 160 | 20706.47 | 385814.2107
5200-Reduction gear B | 4 | 4 | 478 | 98975.1332
5201-Load shaft and bearings A | 20 | 20 | 1955.4 | 297291.5042
5205-Main coupling between the turbine and generator A | 7 | 7 | 508 | 2043.5331
5206-Gas Turbine Clutch | 28 | 28 | 4075.53 | 149713.7641
5210-Intercoolers A | 19 | 19 | 2228.5 | 62022.3225
5220-Regenerators A | 1 | 1 | 45 | 716.25
5240-Fire detection and extinguishing system B | 183 | 183 | 23741.56 | 514329.3086
5241-Fire in unit A | 18 | 18 | 2609.71 | 23812.2509
5245-Gas Turbine Control System - data highway | 56 | 56 | 6011.51 | 40444.8193
5246-Gas Turbine Control System - hardware problems (including card failure) | 215 | 215 | 24266.1 | 268458.7919
5247-Gas Turbine Control System - internal and termination wiring | 44 | 45 | 3658.38 | 54753.8412
5248-Gas Turbine Control System - logic problems | 115 | 116 | 12218.24 | 274177.7182
5249-Gas Turbine Control System - upgrades | 39 | 39 | 5360.54 | 96621.838
5250-Other Controls and instrumentation Problems A | 428 | 433 | 54513.63 | 1143563.3861
5255-Computer | 20 | 20 | 2085.59 | 66384.7409
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 24 | 24 | 3834.1 | 379989.1332
5261-Gas turbine/compressor washing | 17 | 17 | 2409.96 | 53012.8195
5262-Gas turbine exchange | 3 | 3 | 231 | 87798.1
5269-Combustion inspection (CI) | 3 | 3 | 467 | 47724.0333
5270-Hot end inspection B | 8 | 8 | 1349.9 | 304590.0663
5272-Boroscope inspection A | 14 | 14 | 1061.8 | 193365.9332
5274-General unit inspection A | 34 | 34 | 2022.24 | 126478.8209
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 56 | 56 | 3847.87 | 669402.182
5285-Gas turbine vibration | 207 | 209 | 18549.79 | 3108018.0653
5286-Gas Turbine lockout cause by OEM specifications | 20 | 20 | 2269.52 | 6463.6973
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 28 | 30 | 1281.35 | 36819.4777
5295-Synchronous condenser equipment A | 4 | 5 | 211 | 428.3
5298-Main gas filter | 7 | 7 | 853 | 11484.0532
5299-Other miscellaneous gas turbine problems | 523 | 531 | 56090.02 | 2717660.6091
5400-Inlet air ducts B | 5 | 5 | 200.1 | 11133.9999
5401-Inlet air vanes/noozles | 6 | 6 | 303.4 | 37629.3732
5402-Inlet air filters B | 2 | 2 | 100 | 176.6667
5403-Inlet and exhaust cones | 1 | 1 | 95 | 51045.0833
5404-Inlet air chillers A | 23 | 24 | 273.09 | 8581.3562
5405-Inlet air evaporative coolers A | 3 | 3 | 44.55 | 6159.105
5406-Inlet air foggers A | 1 | 1 | 9 | 639
5409-Other inlet air problems B | 21 | 21 | 981.12 | 17131.821
5412-High pressure blades/buckets C | 13 | 13 | 677.3 | 304189.4199
5413-Other high pressure problems D | 15 | 15 | 615.9 | 15545.5498
5414-Compressor diaphragms/vanes | 12 | 12 | 361 | 5498.9499
5422-Low pressure blades/buckets C | 6 | 6 | 209.4 | 143347.57
5429-Other low pressure problems D | 10 | 10 | 481.36 | 6875.0301
5430-Supercharging fans B | 1 | 1 | 50 | 6.6666
5436-Compressor shaft & bearings two shaft machines | 2 | 2 | 31.73 | 319.2192
5439-Jet engine other compressor problems | 22 | 22 | 1402.7 | 75394.2845
5440-Fuel tanks A | 1 | 1 | 45 | 22.5
5441-Fuel piping and valves B | 172 | 175 | 8033.78 | 473063.7292
5442-Fuel nozzles/vanes A | 17 | 17 | 837.1 | 14366.7198
5443-Fuel filters B | 7 | 7 | 268 | 20142.3666
5444-Liquid fuel oil pump B | 11 | 11 | 291.2 | 16434.6158
5445-Liquid fuel oil transfer/forwarding pump A | 5 | 5 | 260.4 | 27189.9066
5446-Liquid fuel purge system B | 2 | 2 | 73.7 | 414.3517
5447-Gas fuel system A | 142 | 142 | 8445.48 | 179304.7433
5449-Other fuel system problems A | 84 | 85 | 3204.21 | 40955.7448
5450-Ignition system B | 42 | 42 | 3075.56 | 16371.4435
5451-Pilot fuel piping and valves B | 3 | 4 | 122.9 | 327.5133
5454-Water injection system (Jet Engine) | 75 | 75 | 3314.9 | 24238.8138
5455-Fuel nozzle/vane cooling air system | 5 | 5 | 140.1 | 12978.6433
5460-Atomizing air system A | 2 | 2 | 139 | 275.4666
5470-Combustor casing B | 1 | 1 | 41 | 984
5471-Combustor liner A | 3 | 3 | 148.79 | 38883.3888
5473-Flame scanners A | 17 | 17 | 735.27 | 1212.8418
5474-Flashback (including instrumentation) | 3 | 3 | 126.79 | 558.1274
5475-Blade Path Temperature Spread B | 34 | 38 | 4463.15 | 42875.7287
5479-Other combustor problems A | 31 | 31 | 1097.2 | 4381.328
5480-High pressure shaft A | 3 | 3 | 410 | 8673.1998
5481-High pressure bearings A | 2 | 2 | 80 | 4265.9166
5482-High pressure blades/buckets D | 8 | 8 | 471.5 | 241795.2748
5483-High pressure nozzles/vanes B | 3 | 3 | 396.8 | 35105.3398
5486-High pressure shaft seals B | 2 | 2 | 228 | 10028.1999
5487-Thrust Bearing/jet | 2 | 2 | 109.4 | 189.065
5489-Other high pressure problems C | 10 | 10 | 325.7 | 13432.9899
5490-Low pressure shaft B | 2 | 2 | 121 | 7002.4333
5491-Low pressure bearings C | 2 | 2 | 116 | 3522.5666
5492-Low pressure blades/buckets B | 6 | 6 | 270 | 26914.5
5493-Low pressure nozzles/vanes A | 3 | 3 | 138 | 89659.9666
5497-Other low pressure problems C | 3 | 3 | 162.2 | 5300.215
5499-Shaft seals A | 1 | 1 | 36 | 48.6
5501-Hoods A | 1 | 1 | 112 | 3559.7333
5502-Vanes/nozzles B | 1 | 1 | 70 | 63
5503-Silencer A | 8 | 8 | 266 | 5437.7999
5505-Diverter Dampers A | 2 | 2 | 109 | 877.45
5508-High engine exhaust temperature B | 32 | 32 | 1329.1 | 10110.5696
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 26 | 26 | 1345.6 | 12065.6081
5510-Lube oil system A | 154 | 154 | 7195.16 | 156604.5879
5516-Power Augmentation System Equipment A | 18 | 18 | 905.5 | 37773.2964
5520-Hydraulic oil system B | 43 | 43 | 2236.76 | 31965.0579
5530-Starting system (including motor) B | 58 | 60 | 3211.1 | 65911.9924
5540-Battery and charger system A | 6 | 6 | 264 | 2970.3499
5550-Turning gear and motor B | 3 | 3 | 258.9 | 13746.7049
5551-Load gear compartment A | 3 | 3 | 158 | 3263.5
5560-Cooling and seal air system A | 32 | 32 | 1755.5 | 27369.2844
5570-Cooling water system B | 23 | 23 | 713.5 | 3867.8313
5580-Anti-icing system B | 24 | 25 | 1052.65 | 7990.2605
5590-Other auxiliary system problems B | 61 | 61 | 2294 | 146068.9225
5600-Reduction gear A | 3 | 3 | 92.95 | 2305.5808
5601-Load shaft and bearings B | 3 | 3 | 238 | 377.3999
5606-Jet Engine Clutch | 10 | 10 | 611.19 | 4080.6206
5610-Intercoolers B | 1 | 1 | 112 | 24.2666
5640-Fire detection and extinguishing system A | 41 | 41 | 2233.5 | 23442.6009
5645-Jet Engine Control System - data highway | 39 | 39 | 1218.95 | 4538.0321
5646-Jet Engine Control System - hardware problems (including card failure) | 72 | 72 | 3448.2 | 26176.1088
5647-Jet Engine Control System - internal and termination wiring | 22 | 27 | 991.9 | 5602.3914
5648-Jet Engine Control System - logic problems | 26 | 26 | 1025.9 | 7300.6464
5649-Jet Engine Control System - upgrades | 1 | 1 | 58 | 74965
5650-Other Controls and instrumentation Problems B | 181 | 189 | 6732.24 | 68064.7425
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 1 | 1 | 146 | 65.7
5662-Engine exchange | 5 | 5 | 225.9 | 30307.0016
5665-Engine shafts and bearings | 7 | 7 | 371.2 | 43614.0249
5672-Boroscope inspection B | 6 | 6 | 485.4 | 1971.3833
5674-General unit inspection B | 27 | 27 | 1289.6 | 110143.7897
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 26 | 26 | 1045.88 | 42220.6443
5685-Engine vibration | 83 | 83 | 3835.72 | 388850.7211
5686-Jet Engine lockout cause by OEM specifications | 11 | 11 | 489.25 | 16204.4973
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 16 | 17 | 306 | 78214.4499
5699-Other miscellaneous jet engine problems | 78 | 79 | 3217.76 | 362257.9977
5710-Cylinders | 17 | 18 | 151.61 | 26803.2859
5711-Cylinder heads | 7 | 7 | 63 | 23.4333
5731-Exhaust valves | 3 | 3 | 52 | 755.9666
5740-Turbo charger | 1 | 1 | 20.5 | 7226.25
5759-waste gate | 1 | 1 | 9.04 | 25.312
5799-Other engine problems | 35 | 45 | 344.31 | 3766.0266
5800-Lube oil system C | 2 | 2 | 5.07 | 133.1603
5805-Cooling system | 25 | 25 | 259.28 | 8461.1826
5810-Heater elements | 1 | 3 | 2.57 | 0.85667
5811-HT water pre heater | 1 | 1 | 9.04 | 490.5707
5815-Fuel system | 23 | 24 | 422.26 | 943.0553
5820-Start system | 13 | 13 | 135.03 | 735.5581
5849-Other engine auxiliaries problems | 10 | 10 | 144.16 | 2306.5266
5850-Governor | 1 | 1 | 2 | 94.0333
5855-Engine control system | 33 | 34 | 395.68 | 2016.6494
5865-Synchronization system | 1 | 1 | 2.57 | 56.5828
5870-Other engine control problems | 6 | 6 | 41.36 | 938.0462
5874-Exhaust gas temp sensor | 1 | 1 | 9.04 | 6.6293
5895-Inspection C | 1 | 1 | 9.04 | 6.78
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 194 | 233 | 4299.05 | 41536.9793
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 22 | 22 | 3603.54 | 14467.1686
6005-HP Evaporator tubes | 22 | 22 | 4411.69 | 304437.854
6006-IP Evaporator tubes | 2 | 2 | 225 | 5765
6007-LP Evaporator tubes | 7 | 7 | 1106.49 | 117462.2513
6010-HP superheater | 25 | 25 | 5343.83 | 430151.9791
6011-HP reheater | 9 | 9 | 1239.99 | 61209.0013
6012-HP economizer | 39 | 39 | 6062.6 | 494372.5067
6020-IP superheater | 8 | 8 | 1495 | 70614.7828
6021-IP reheater | 24 | 24 | 3489 | 490269.4823
6022-IP economizer | 5 | 5 | 1470 | 68271.1076
6030-LP reheater | 6 | 6 | 776.57 | 54467.6916
6032-LP economizer | 12 | 12 | 1510.6 | 73720.9498
6090-Other HRSG tube Problems | 14 | 14 | 2813.6 | 96420.7558
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 3 | 3 | 1251 | 1487.2997
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 21 | 21 | 3286.2 | 198191.1759
6111-HP steam relief/safety valves | 7 | 7 | 540.8 | 30905.1831
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 56 | 56 | 8798.2 | 132343.6769
6113-Other HP steam system problems | 12 | 12 | 2552 | 38822.2657
6114-HP steam isolation/boundary valves | 42 | 42 | 8453.89 | 218528.5291
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 2 | 2 | 632.53 | 14518.4492
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 1 | 1 | 157.5 | 2128.8749
6123-Other IP steam system problems | 11 | 11 | 1411.72 | 2954.7736
6124-IP steam isolation/boundary valves | 10 | 10 | 2358.08 | 20714.3116
6130-LP steam piping up to turbine stop valves - Less than 200 PSIG (see 0790 for piping supports) | 5 | 5 | 1309 | 18849.1328
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 9 | 9 | 1430.14 | 12771.5366
6133-Other LP steam system problems | 36 | 36 | 2077.09 | 49315.0612
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 29 | 29 | 5184.5 | 119107.4064
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 2 | 2 | 257 | 13166.9666
6141-HP Desuperheater/attemperator valves | 48 | 48 | 9500.52 | 58584.5981
6144-Other HP desuperheater/attemperator problems | 9 | 9 | 1928.14 | 2369.8346
6146-IP Desuperheater/attemperator valves | 11 | 11 | 1876.78 | 4349.6921
6147-IP Desuperheater/attemperator spray nozzles | 2 | 2 | 250 | 4904.1665
6149-Other IP desuperheater/attemperator problems | 1 | 1 | 381 | 374.6499
6151-LP Desuperheater/attemperator valves | 2 | 2 | 189.4 | 6670.0832
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 3 | 3 | 775.9 | 29538.2997
6161-HP Startup bypass system valves | 36 | 36 | 8017.84 | 115745.6512
6162-HP Startup bypass tanks or flash tanks | 1 | 1 | 218 | 3070.1666
6163-Other HP startup bypass system problems | 4 | 4 | 831 | 7848.8663
6164-HP Startup bypass instrumentation and controls | 23 | 23 | 5335.53 | 57134.6058
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 2 | 2 | 481 | 5403.8332
6171-IP Startup bypass system valves | 55 | 55 | 11474.74 | 469819.3141
6174-IP Startup bypass instrumentation and controls | 19 | 19 | 3222.37 | 55004.5223
6180-LP Startup bypass system piping (including drain lines up to heaters or condenser) - Less than 200 PSIG | 1 | 1 | 381 | 14306.55
6181-LP Startup bypass system valves | 4 | 4 | 936 | 739.3162
6184-LP startup bypass instrumentation and controls | 1 | 1 | 156 | 257.4
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 96 | 96 | 16487.95 | 179542.7139
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 47 | 48 | 6710.7 | 161909.4755
6410-Steam wells/steam field piping problems | 4 | 4 | 63 | 225.2167
6420-Condensate reinjection system | 28 | 28 | 201 | 66502.1833
6440-H2S abatement system problems ? general | 4 | 4 | 139 | 1002.65
6480-Steam strainer plugging ? mineral deposits | 1 | 1 | 55 | 12516.1666
6499-Geothermal | 3 | 3 | 90 | 288.7166
7000-Shaft B | 8 | 8 | 990.58 | 175005.6951
7001-Shaft packing | 39 | 39 | 3788.74 | 777925.5991
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 23 | 23 | 3584.19 | 938266.4813
7007-Bearings A | 43 | 43 | 2509.91 | 440915.9141
7008-Bearing cooling system B | 43 | 44 | 2717.11 | 107889.5307
7009-Bearing Oil System | 72 | 72 | 5627.92 | 411145.1404
7010-Runner cavitation damage | 5 | 5 | 383.52 | 221724.5999
7011-Other runner problems | 10 | 10 | 800.19 | 559195.1353
7012-Casing; wear ring; or liner cavitation damage | 1 | 1 | 23.75 | 3779.4167
7020-Nozzle assembly | 3 | 3 | 214.74 | 1430.082
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 32 | 32 | 1809.63 | 482471.1564
7040-Turbine overhaul | 1 | 1 | 43.26 | 4946.06
7050-Turbine governor | 168 | 170 | 16447.89 | 799778.5964
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 40 | 40 | 4730.16 | 562159.6041
7053-Governor Oil System | 123 | 126 | 9552.63 | 542185.1921
7099-Other turbine problems | 119 | 121 | 5501.82 | 1747815.9588
7100-Upper reservoir dams and dikes | 6 | 6 | 293.3 | 1692.8932
7101-Lower reservoir dams and dikes | 12 | 12 | 270.7 | 28564.7553
7110-Intake channel or flume (including trash racks) | 178 | 190 | 5865.02 | 333761.9748
7111-Intake tunnel | 33 | 33 | 4608 | 160038.9315
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 11 | 11 | 227.2 | 4271.2766
7120-Headgates | 28 | 28 | 1529.59 | 46019.0228
7121-Shutoff valves | 44 | 45 | 5233.26 | 324822.5043
7123-Shutoff valve bypass line and valve | 4 | 4 | 435.25 | 1987.3666
7124-Penstock | 24 | 24 | 1850.51 | 216785.5991
7130-Spiral case | 5 | 5 | 824 | 111439.2331
7140-Wicket gate assembly | 10 | 10 | 1219.07 | 44937.639
7141-Wicket gate operating mechanism or positioner | 35 | 35 | 2807.85 | 106173.0278
7142-Wicket gate shear pin | 117 | 117 | 7095.88 | 151502.0194
7160-Pressure regulating valve | 9 | 9 | 394.37 | 154361.034
7161-Pressure regulating valve operator or positioner | 1 | 1 | 77 | 32338.7166
7162-Relief valve and vacuum breakers | 1 | 1 | 43 | 75.9666
7170-Draft tube | 10 | 10 | 973.89 | 328775.9386
7180-Tailrace | 36 | 36 | 1044.08 | 212944.4702
7181-Tail water depressing equipment | 10 | 10 | 1187.76 | 21300.3415
7190-Dewatering and rewatering equipment | 9 | 9 | 1461.35 | 28923.8209
7191-Equalizing line | 3 | 3 | 1212 | 155600.5996
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 109 | 109 | 2497.13 | 315208.1115
7201-Inspection A | 8 | 8 | 260.09 | 2452.8155
7210-Canals (including siphons; radial gates; and spills) | 1 | 1 | 41 | 131.2
7230-Pony motor (pumped storage units only) | 4 | 4 | 1260 | 6199.6326
7240-Powerhouse Substructure | 2 | 2 | 47.5 | 24453.7917
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 30 | 32 | 2866.36 | 59661.0391
7300-Routine Hydro Planned Outage (reoccuring schedule) | 3 | 3 | 280 | 1893.3166
7800-Couplings | 1 | 1 | 95 | 387.9166
7810-Shaft A | 2 | 2 | 120 | 2048.9999
7820-Bearings B | 9 | 9 | 355.07 | 214336.4483
7830-Blades | 4 | 4 | 56 | 60480
7890-Seal oil system and seals B | 3 | 3 | 264 | 1401.0499
7920-Lube oil system B | 7 | 7 | 339 | 35310.1999
7930-Controls and instrumentation A | 20 | 20 | 1079.49 | 8224.0913
7960-Other expander turbine problems | 4 | 4 | 146.4 | 2333.8599
8000-Chemical feed storage; mill feeders; and conveyors | 38 | 38 | 16106.11 | 159450.4316
8002-Screw conveyors | 2 | 2 | 700 | 1458.3331
8003-Bucket elevators | 3 | 3 | 2025 | 8010.1658
8010-Crushers/mills | 26 | 26 | 14015 | 76253.9117
8020-Mill slurry tanks supply problems | 10 | 10 | 3855 | 16479.4987
8030-Classifiers | 1 | 1 | 150 | 75
8040-Slurry transfer pumps and motors | 6 | 6 | 1054.27 | 4328.9107
8050-Chemical unavailability | 1 | 1 | 18.3 | 73.2
8099-Other chemical supply problems | 12 | 12 | 2253 | 85062.2825
8100-Scrubber/absorber tower or module | 47 | 47 | 9769.07 | 519466.3335
8110-Spray nozzles | 6 | 6 | 849 | 10419.6664
8120-Spray pumps and motors | 12 | 12 | 2818 | 25562.349
8125-Scrubber recycle (liquid) pumps | 14 | 14 | 2005 | 35454.4827
8127-Scrubber recycle (liquid) pump motors | 3 | 4 | 424.27 | 7358.3399
8130-Recirculation tanks including agitators | 6 | 6 | 1457 | 63094.6999
8140-Reaction tanks including agitators | 5 | 5 | 1145 | 57858.5997
8150-Tubes | 3 | 3 | 613.3 | 72896.9414
8160-Mist eliminators/demisters and washdown | 60 | 60 | 5972.8 | 461410.7995
8199-Other scrubber problems | 83 | 83 | 25686.24 | 326260.5666
8200-Piping | 15 | 15 | 3383.82 | 33866.7764
8210-Valves | 5 | 5 | 882.76 | 2227.0416
8220-Strainers or filters | 2 | 2 | 923.13 | 19866.2723
8230-Ducting | 7 | 7 | 2118.28 | 162926.4948
8235-Demister | 11 | 11 | 297 | 72.8999
8240-Bypass dampers | 1 | 1 | 299 | 877.0666
8250-Dampers other than bypass | 6 | 6 | 2106.63 | 39528.1023
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 29 | 29 | 5216.89 | 127393.9199
8261-Scrubber booster I.D. fan drive | 4 | 4 | 757 | 39716.8496
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 8 | 8 | 1049 | 23674.7665
8265-Scrubber ID fan dampers | 3 | 3 | 165.16 | 792.9546
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 24 | 24 | 1176.74 | 26380.9709
8271-Scrubber booster F.D. fan drive | 3 | 3 | 520 | 37768.3333
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 1 | 1 | 215 | 24402.5
8280-Reagent feed piping | 5 | 5 | 1219 | 1825.3326
8299-Other piping; ducting; damper; and fan problems | 5 | 5 | 2320 | 68066.9993
8330-Dewatering equipment (thickener; centrifuge; etc.) | 32 | 32 | 17261.51 | 1079928.0496
8340-Centrifuge/vacuum filter | 1 | 1 | 423.16 | 2990.3304
8349-Other waste disposal and recovery problems | 1 | 1 | 529 | 16108.05
8399-Solids conveying and mixing system problems | 3 | 3 | 1125 | 16458.9996
8404-Scrubber gas discharge reheaters - tube leaks | 1 | 1 | 80 | 138.6666
8410-Scrubber instruments and controls | 10 | 10 | 2670.45 | 19102.811
8415-Liquid level controls | 2 | 2 | 360 | 110.3332
8425-Miscellaneous mechanical failures | 4 | 4 | 658 | 18151.0162
8426-Miscellaneous electrical failures | 6 | 6 | 1591 | 3046.3
8460-Testing | 3 | 3 | 1037 | 3448.5831
8470-SO2 monitor | 1 | 1 | 50 | 825.8333
8499-Other miscellaneous wet scrubber problems | 84 | 84 | 2832.15 | 39171.4536
8500-Slurry storage and feed tanks | 4 | 4 | 1338.4 | 8192.1413
8501-Reagent storage; feed bins; and conveyors | 1 | 1 | 70 | 43.1666
8504-Mills/slakers | 1 | 1 | 187 | 2044.5333
8505-Scalping screens | 1 | 1 | 194 | 905.3332
8506-Slurry pipelines | 2 | 2 | 238 | 1743.5
8508-Reagent unavailability | 1 | 1 | 20 | 360
8510-Slurry mixers and agitators | 1 | 1 | 18.3 | 68.625
8520-Slurry transfer pumps and motors | 2 | 2 | 645 | 1171.7498
8521-Reagent/slurry problems | 7 | 7 | 1439.16 | 9373.3235
8522-Piping | 2 | 2 | 342 | 3755.9998
8523-Valves | 4 | 4 | 1122 | 5845.1999
8524-Strainers or filters | 8 | 8 | 1981.1 | 54999.4909
8525-Ducting | 2 | 2 | 28 | 26775
8526-Dampers | 1 | 1 | 49 | 559.4166
8527-Other piping; ducting; and damper problems | 2 | 2 | 96 | 2771.9999
8528-Dry scrubber instruments and controls | 8 | 8 | 4261 | 70785.4816
8529-Gas dispersers | 3 | 3 | 129.2 | 2421.4916
8530-Spray towers | 9 | 9 | 661 | 38457.2165
8531-Spray machine/atomizer | 46 | 48 | 4440.54 | 57688.2352
8532-Spray machine/atomizer motors | 3 | 3 | 398 | 994
8533-Spray machine/atomizer lubrication systems | 1 | 1 | 320 | 688
8534-Spray machine/atomizer vibration problems | 13 | 14 | 1256 | 115837.5827
8535-Fly ash conveyors | 5 | 5 | 472.22 | 4759.4781
8538-Recycle storage and feed tanks including agitators | 3 | 3 | 1206 | 9849.9994
8542-Recycle feed bins aeration systems | 1 | 1 | 320 | 1680
8544-Mechanical failures | 3 | 3 | 655 | 63890.6331
8545-Electrical failures | 7 | 7 | 1404.93 | 20797.167
8547-Inspection | 4 | 4 | 501 | 1524.6666
8549-Other dry scrubber problems | 9 | 9 | 1779 | 7835.4159
8550-Electrostatic precipitator fouling | 28 | 28 | 2882 | 50813.1656
8551-Electrostatic precipitator field out of service | 59 | 62 | 4095 | 130040.6653
8560-Electrostatic precipitator problems | 103 | 103 | 9708.89 | 271787.5334
8570-Mechanical precipitator fouling | 7 | 9 | 170 | 47435.3333
8580-Mechanical precipitator problems | 1 | 1 | 226 | 2022.7
8590-Other precipitator problems | 8 | 8 | 1072 | 31484.2495
8600-Flue gas additives (furnace injection) | 1 | 1 | 47 | 1034
8601-SO3 mitigation | 13 | 13 | 2673 | 10819.9492
8620-Mercury Abatement | 4 | 4 | 1312 | 1340378.966
8650-Baghouse systems; general | 160 | 160 | 10816.5 | 1094628.1071
8651-Bag failures and rebagging | 173 | 174 | 7140.09 | 450384.2196
8652-Shakers and rappers | 2 | 2 | 138 | 1603.3667
8654-Baghouse booster fans and motors | 56 | 56 | 7007.5 | 145686.0181
8655-Structural duct work and dampers | 17 | 17 | 1817.06 | 79213.1724
8656-Controls and instrumentation B | 66 | 66 | 3998.22 | 68046.388
8657-Ash handling system and hoppers | 41 | 41 | 7144.88 | 133840.9305
8670-Emission monitors (other than CEMS) A | 1 | 1 | 201 | 2117.1999
8699-Other miscellaneous pollution control equipment problems | 51 | 51 | 9238.91 | 379442.4885
8700-CEMS Certification and Recertification | 34 | 34 | 4196.5 | 129384.8071
8710-SO2 analyzer problems | 2 | 2 | 395 | 956.25
8720-NOx analyzer problems | 69 | 69 | 6215.17 | 42696.8983
8730-CO analyzer problems | 28 | 28 | 3425.73 | 64642.5908
8740-CO2 analyzer problems | 3 | 3 | 421.6 | 12447.8831
8750-O2 analyzer problems | 20 | 20 | 1727.02 | 57769.9098
8760-Opacity monitor problems | 25 | 25 | 2900.85 | 38651.7424
8770-Flow monitor problems | 9 | 9 | 652.85 | 17537.7372
8780-Data acquisition system problems | 41 | 41 | 3955.14 | 43002.377
8790-Miscellaneous CEMS problems | 139 | 143 | 9842.12 | 98207.2341
8802-SNCR NOx Control system | 40 | 40 | 4024.56 | 12125.6682
8809-Other SNCR NOx problems | 15 | 15 | 578.7 | 2752.2832
8810-SCR NOx Reactor | 10 | 10 | 285 | 10038.1166
8812-SCR NOxCatalyst | 31 | 31 | 1334.6 | 176740.3462
8813-SCR NOx Injection grid piping/valves | 26 | 26 | 1416.47 | 12870.5493
8814-SCR NOx Catalyst support material | 1 | 1 | 63.79 | 328.5185
8815-SCR NOx Soot blowers | 3 | 3 | 297.6 | 512.5332
8816-SCR NOx Plugging | 26 | 26 | 1206.09 | 116840.5318
8817-SCR NOx Control system | 123 | 123 | 9107.75 | 210432.9672
8820-SCR NOx Ammonia injection grid piping/valves | 71 | 72 | 8056.71 | 130477.0917
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 78 | 78 | 7601.21 | 78844.8271
8822-SCR NOx Ammonia air blowers | 31 | 31 | 3148.76 | 34316.3447
8823-SCR NOx Other ammonia system problems | 94 | 94 | 10869.88 | 129890.3407
8825-Other SCR NOx problems | 88 | 89 | 7366.66 | 144533.0258
8832-CAH NOx Plugging | 1 | 1 | 78 | 46215
8835-CAH NOx Other CAH problems | 2 | 2 | 317 | 1535.3
8840-CO Active catalyst | 10 | 10 | 429.7 | 18159.0215
8842-CO Plugging | 2 | 2 | 281 | 2133.0833
8845-Other CO reduction problems | 45 | 46 | 2333.22 | 12711.3445
9000-Flood | 108 | 108 | 5322.07 | 1058518.2409
9010-Fire; not related to a specific component | 56 | 56 | 4109.98 | 802986.5302
9020-Lightning | 205 | 205 | 25024.63 | 488802.1393
9030-Earthquake | 3 | 3 | 96 | 862.7
9031-Tornado | 5 | 5 | 811 | 542.9998
9035-Hurricane | 27 | 27 | 5465.84 | 210423.4392
9036-Storms (ice; snow; etc) | 135 | 136 | 9277.14 | 398288.0706
9040-Other catastrophe | 117 | 185 | 16690.59 | 325077.2942
9110-Core coastdown (nuclear) | 1 | 1 | 3.4 | 21.25
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 701 | 818 | 64483.61 | 4416676.2795
9131-Lack of fuel: Contract or Tariff allows for interruption | 560 | 677 | 64643.19 | 5759967.2249
9132-Wet Fuel - Biomass | 217 | 246 | 1519.53 | 8696.2825
9134-Fuel conservation | 59 | 59 | 7213.82 | 198963.1012
9135-Lack of water (hydro) | 2116 | 2270 | 34138.84 | 1124715.9749
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 12 | 12 | 1003.8 | 17084.8597
9137-Ground water or other water supply problems | 85 | 85 | 3433.9 | 59866.5822
9140-Plant modifications to burn different fuel (not regulatory mandated) | 3 | 3 | 525.8 | 5745.3
9150-Labor strikes company-wide problems or strikes outside the company's jurisdiction such as manufacturers (delaying repairs) or transportation (fuel supply) problems. | 15 | 15 | 284.4 | 11034.3882
9160-Other economic problems | 7 | 7 | 282 | 11562.5499
9180-Economic (for internal use at plants only) | 3 | 3 | 206.7 | 26128.6504
9181-Economic (for internal use at plants only) | 3 | 3 | 1849 | 15324.3661
9182-Economic (for internal use at plants only) | 24 | 24 | 10704 | 44712.0298
9200-High ash content | 70 | 70 | 2438.11 | 52111.8258
9205-Poor quality natural gas fuel; low heat content | 1 | 1 | 26 | 3345.3333
9210-Low grindability | 32 | 32 | 2035.24 | 34198.4993
9220-High sulfur content | 58 | 58 | 5233.88 | 30930.4755
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 382 | 383 | 9237.38 | 264772.0078
9251-Low Btu Coal From Contract For Low Btu Coal | 30 | 30 | 1038.01 | 20120.0776
9260-Low Btu oil | 4 | 4 | 19.5 | 298.9
9270-Wet coal | 1015 | 1029 | 100279.07 | 1819210.3106
9271-Wet coal (not outside management control) | 357 | 359 | 53878.32 | 434449.7727
9272-Wet Fuel (other than coal) | 19 | 20 | 90.54 | 277.5507
9280-Frozen coal | 58 | 58 | 8248.18 | 54660.3023
9281-Frozen coal (not outside management control) | 7 | 7 | 1698.57 | 24276.4818
9290-Other fuel quality problems | 230 | 231 | 17226.74 | 605637.5122
9291-Other fuel quality problems (not outside management control) | 124 | 124 | 6962.07 | 88857.215
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 1067 | 1086 | 92016.75 | 3030051.3634
9305-Ash disposal problem | 3 | 3 | 620.64 | 9916.8453
9320-Other miscellaneous external problems | 698 | 919 | 29782.26 | 3536277.6809
9345-Pumping Operations | 1 | 1 | 25 | 448.3333
9350-Public Safety/River Rescue | 8 | 8 | 300.4 | 717.6928
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 26 | 26 | 6346.51 | 4432438.3438
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 70 | 72 | 5776.31 | 675297.0553
9600-SO2 stack emissions (fossil) | 137 | 138 | 15070.6 | 135034.0984
9603-SO2 stack emissions (gas turbine) | 2 | 2 | 121 | 1083.8833
9610-NOx stack emissions (fossil) | 63 | 63 | 3170.87 | 115185.6846
9613-NOx stack emissions (gas turbine) | 132 | 132 | 10916.3 | 87544.8333
9614-NOx stack emissions (jet engines) | 49 | 51 | 2084.08 | 10285.3116
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 4 | 4 | 14.3 | 116.1442
9616-CO stack emissions | 195 | 227 | 7609.01 | 106188.9764
9620-Particulate stack emissions (fossil) | 32 | 32 | 2767.5 | 93489.8526
9630-Opacity (fossil) | 457 | 466 | 38823.12 | 700146.5641
9634-Opacity (jet engines) | 2 | 2 | 90 | 1342.4999
9650-Other stack or exhaust emissions (fossil) | 42 | 42 | 1631 | 13792.7494
9653-Other stack or exhaust emissions (gas turbine) | 35 | 35 | 3311.38 | 87244.9876
9654-Other stack or exhaust emissions (jet engines) | 2 | 2 | 108 | 9312.2
9656-Other stack or exhaust emissions testing - fossil | 8 | 8 | 1205.4 | 11327.2164
9657-Other stack or exhaust emissions testing - gas turbine | 13 | 13 | 2665.85 | 37650.515
9658-Other stack or exhaust emissions testing - jet engines | 5 | 5 | 290 | 2390.4333
9660-Thermal discharge limits (fossil and nuclear) | 52 | 53 | 3859.78 | 153326.9641
9663-Thermal discharge limits (gas turbine) | 1 | 1 | 62.4 | 45.76
9680-Fish kill (fossil and nuclear) | 3 | 3 | 1956 | 6687.7996
9686-Fish kill (hydro and PS) | 2 | 2 | 29.4 | 14145.4833
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 73 | 73 | 2702.44 | 214169.7016
9693-Other miscellaneous operational environmental limits (gas turbines) | 30 | 30 | 3017.5 | 204712.2407
9694-Other miscellaneous operational environmental limits (jet engines) | 38 | 44 | 572.32 | 3629.6787
9696-Other miscellaneous operational environmental limits (hydro and PS) | 31 | 31 | 434 | 20662.704
9720-Other safety problems | 52 | 52 | 3344.46 | 1186705.5822
9900-Operator error | 408 | 408 | 95998.05 | 856923.3694
9910-Maintenance personnel error | 127 | 127 | 22763.64 | 781662.3471
9920-Contractor error | 65 | 65 | 14809.24 | 231099.8777
9930-Operating procedure error | 68 | 69 | 16573.95 | 972292.5442
9940-Maintenance procdure error | 28 | 28 | 5310.64 | 66908.9502
9950-Contractor procedure error | 12 | 12 | 2667.32 | 52096.8462
9960-Staff shortage | 18 | 18 | 2030.1 | 136217.0931
9997-NERC Reliability Standards requirements | 8 | 8 | 843.5 | 3342.4166
9998-Black Start testing | 3 | 3 | 171.5 | 2247.2416
9999-Total unit performance testing (use appropriate codes for individual component testing) | 194 | 202 | 4354.69 | 2088556.5626
Total Result | 59143 | 61426 | 7366943.06 | 356829324.0887

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 28 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 12 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.8667 | 22 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.4667 | 16 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 612 | 102 | 1 | 1 | 0010-Thaw shed failure or fire | U1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.3333 | 28 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.1 | 9 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 740.4 | 72 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 567.3833 | 59 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.0333 | 23 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 418.5 | 31 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 12.4 | 6.2 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 90 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 386.8333 | 211 | 2 | 2 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1727.9996 | 648 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 81 | 8.1 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Summer | 53.0667 | 19.9 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2039.2166 | 227 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7648 | 64 | 1 | 1 | 0024-Rotary plow | D2-Forced - Delayed | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 170.85 | 51 | 1 | 1 | 0024-Rotary plow | U1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 34.1 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1365.7832 | 227 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 52.5 | 21 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12073.25 | 105 | 1 | 1 | 0028-Dust collection system | U1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1217.2999 | 222 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2861.25 | 105 | 1 | 1 | 0028-Dust collection system | U1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38145.4164 | 415 | 1 | 1 | 0028-Dust collection system | U1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6217.1998 | 237.6 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.8333 | 190 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 133.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3080.2332 | 301 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5641.0833 | 139 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9139.6 | 584 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.45 | 87 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 242.6032 | 199.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 880.5332 | 254 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1012.2665 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5856 | 488 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 702 | 117 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3958.3333 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 345.8332 | 415 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4382.6665 | 304 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 73.0667 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.9166 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43065 | 495 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.9999 | 117 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 486.0165 | 241 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 562.4999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2488.5 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3080.1914 | 327.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4058.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.9165 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.5 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 411.2499 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 220 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 231.25 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1981.7 | 149 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2691.4266 | 332.96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3225.55 | 93 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9545 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 67.1666 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2603.1165 | 313 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1791.9997 | 420 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9695.8329 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12759.2 | 328 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.8333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 375 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 976.7999 | 99 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 987.3 | 54 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1033.5833 | 157 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6628.3331 | 820 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 379.8666 | 308 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 401.1666 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 581.0999 | 234 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 720 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2757.333 | 440 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 121.5 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210 | 72 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 273.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 355.8333 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 952.2499 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7981.9997 | 390 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1677.32 | 176.56 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 156.75 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 6 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 190.9666 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2442 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3444.6999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 101.15 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.2667 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 713.9999 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 816.8331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1207.5 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1602.3333 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2083.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2424.5 | 373 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2532 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29028 | 492 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 472 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 994.9331 | 287 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1069.2 | 194.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.7666 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.0666 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1657.5 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2089.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2442.6 | 236 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1282.5 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2546.4998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2550 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2883.5332 | 259 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5785 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 10170.9997 | 420 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 7.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.1 | 62 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 293.75 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 634.6666 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 786.4999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 795.3 | 241 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1172 | 293 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1387.5 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4829.4166 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176.6666 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 742 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 841.6665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 987.36 | 224.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3120 | 520 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10988.9995 | 810 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.76 | 65.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 275 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 564 | 188 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 650 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 842.6666 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1595.9998 | 630 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5674.5 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2145.6998 | 258 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3.6667 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1503.333 | 440 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 331.1 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 114.75 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.3 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2130 | 600 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201 | 67 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 378 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1004.9665 | 413 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.7 | 49 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 257.25 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1420.8331 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1558 | 328 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2517.5 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2546.5666 | 317 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2961.2499 | 345 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5000 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 832.4833 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 139.7333 | 64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2081.25 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.2666 | 64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 340 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 567.5625 | 151.35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 28.1667 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 320.8332 | 385 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2688 | 448 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2779.1666 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 609.5 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 68.9333 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14663.4664 | 472 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7799.3498 | 507 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 494.7 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187.02 | 31.17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210.99 | 70.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668 | 48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 675 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 913.5166 | 59 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1673.5643 | 229.78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2187.6997 | 393 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2902.4 | 48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3040 | 800 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4262.4998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.6 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 521.85 | 213 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3213 | 238 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115.8666 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 292.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 396.0832 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 996.6666 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1937.25 | 315 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2513.3333 | 116 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 747.45 | 151 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 121.0666 | 227 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 17.05 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 80 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.85 | 87 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.7984 | 77.01 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5.6 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 299.1667 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1010.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1784.5 | 415 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 158.1998 | 339 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1341.9 | 497 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.8 | 41 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 574.7498 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2023.6998 | 354 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.4998 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.8332 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 746.2066 | 129.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2680.2499 | 106.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8859.5 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9055.2 | 132 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1004.1665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1815 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1935.5 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14772.9998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 881.2499 | 225 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 497.0239 | 84.72 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 794.3 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 400 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 563.5038 | 246.79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 56.3333 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 37.7166 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 75 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 135 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1218.9 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1.7333 | 104 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5001.5331 | 398 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13833.4132 | 354.4 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 263.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 80.6666 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1575.5831 | 365 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 60 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 258.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2142 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 824.0331 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 16716.6666 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4142.6 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3100.6 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 270.5999 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2573.4332 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1215.1 | 419 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.9166 | 161 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 75 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.7166 | 150.2 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.2839 | 118.02 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.7324 | 97.05 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 404.6 | 42 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 588.4666 | 126.1 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 96.1345 | 8.47 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.8333 | 65 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2863.3332 | 200 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 876 | 144 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 835.905 | 37.71 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3051.9 | 101.73 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 640 | 160 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2200 | 220 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 760 | 80 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4913.0666 | 329 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 452.5 | 15 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 82 | 30 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.5 | 30 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1003.7499 | 165 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 546.4166 | 79 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 8.5 | 3 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 153.3333 | 40 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2952 | 40 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.3 | 99 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.5 | 54 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 181.25 | 25 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 401.1 | 21 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 268.3666 | 97 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 514 | 40 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 221.6332 | 218 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3090.6693 | 750.77 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.2 | 48 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.8333 | 50 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50 | 25 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 538.9333 | 16 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 800-Miscellaneous
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 55.1 | 19 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.9998 | 360 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1651.3 | 98 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.6664 | 340 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2588.6665 | 440 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 39.4833 | 23 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 255 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 975 | 50 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1528.8666 | 323 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 4.8333 | 10 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 51.6666 | 31 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 5.8333 | 5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2 | 6 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 579.3333 | 220 | 2 | 2 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 15.8895 | 9.63 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 20.35 | 11 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 90.6667 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 37 | 20 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 75.2 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 85.5666 | 34 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5978.3332 | 340 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2530.5 | 45 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1517.3666 | 98 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.4999 | 390 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1772.9998 | 270 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3643.9666 | 98 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2197.4999 | 225 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 16 | 8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 117.5 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198.1666 | 290 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 0.33333 | 1 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 19.0333 | 2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 64.0333 | 34 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 400.2 | 36 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 261.3331 | 320 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.9 | 18 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 394.4 | 34 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 247.1 | 35.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 61.2 | 15.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 55.8 | 9.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 85.2 | 21.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3682.0667 | 44 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 5 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 404 | 101 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D3-Forced - Postponed | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 194.75 | 15 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1036.9333 | 11 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1771 | 11 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 27.8667 | 15.2 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 22.125 | 17.7 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288 | 96 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D3-Forced - Postponed | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 872.01 | 96.89 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 927.2999 | 99 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 650-Fluidized Bed
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.6392 | 26.69 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 743.3333 | 50 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.05 | 371 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 557.0125 | 202.55 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555 | 150 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9788.5333 | 47 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.8513 | 80.84 | 1 | 1 | 0090-Bunker fires | D3-Forced - Postponed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12942.16 | 152.8 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77953.5998 | 249 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 51.6667 | 20 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6497.6833 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 924.5 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.8 | 42 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.5 | 182 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 169.05 | 69 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 309.75 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 789.3332 | 128 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.5 | 59 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 171.7 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.6 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.8 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115.5 | 63 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 116 | 40 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 158.1 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 182.45 | 123 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 395.6 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 856.8 | 72 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 912.3166 | 67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 4.9167 | 5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 42.6667 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 42 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.6403 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.662 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73.7333 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 688.7999 | 252 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2103.2374 | 277.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2394.4549 | 277.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3795.0724 | 277.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3575 | 250 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.75 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.1667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.7 | 69 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.8 | 71 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 532.8 | 148 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 149.0666 | 104 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6.1333 | 16 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.3333 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.85 | 29 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.4 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.1 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.3 | 42 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.55 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 58.3333 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.7833 | 49 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.15 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.5 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 107.2 | 67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 137.7 | 102 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 219.3333 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 288.6 | 111 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 618 | 103 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2429.5833 | 119 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 16.6458 | 4.25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 40.6333 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1.6 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.775 | 45.3 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 262.2 | 38 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.1166 | 83 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1289.2 | 88 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.5 | 45 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.6666 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1658.5 | 310 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.65 | 113 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 532 | 84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.1333 | 47 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 151.6666 | 91 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.8333 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.4 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.4167 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.7 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.2 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.8 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88.9333 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 96.3333 | 68 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 123.3333 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.65 | 117 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 589.05 | 63 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 721.7 | 42 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 241.2 | 16.08 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 774 | 43 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 917.4163 | 505 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 285.7933 | 65.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1188 | 66 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7090.4833 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.6 | 324 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1958.2967 | 24.92 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.2 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 234.3333 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 618.2999 | 162 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67 | 67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.8333 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.6667 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.8666 | 58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64.35 | 117 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.8333 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 184 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 353.1666 | 65 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 397.15 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 481.4 | 58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 559.45 | 67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 20.9667 | 17 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12089.9616 | 76.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.2087 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1503.905 | 22.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2050 | 250 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.9 | 46 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.4833 | 47 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 140.3 | 61 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 162.9833 | 127 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 207.1666 | 113 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 352 | 64 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1329.3 | 126 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 51.2333 | 58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.25 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.3333 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 140.4 | 52 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 140.6499 | 87 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 147.25 | 57 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 167.1333 | 109 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192.7333 | 49 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 917.7 | 42 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144.3 | 39 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.6666 | 224 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 765.9667 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.3332 | 227 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.25 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 447.9665 | 178 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.4 | 63 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 209.4499 | 177 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1239 | 118 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42 | 36 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.7333 | 77 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.6 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 66.9666 | 49 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78 | 65 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.75 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.4666 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1948 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2698.8166 | 113 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 14.4 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 27.2 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 21.9 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 308.8332 | 170 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57 | 60 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.65 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.7666 | 74 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.5999 | 84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145.75 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.7 | 111 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 806.6666 | 40 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.55 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.7333 | 73 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156.95 | 43 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.3333 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104.4 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 139.3333 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 146.6333 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1591.0333 | 59 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 33.25 | 3.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 27.65 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 335.8333 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.4666 | 148 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7007.7098 | 277.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.4333 | 58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 288.75 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.3 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.2833 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60.1333 | 44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.5 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.7 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 97.9999 | 84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 146.7667 | 17 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 563.2 | 66 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 468.6616 | 28.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 841.4716 | 28.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Summer | 157.5 | 18.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 166.4067 | 22.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 1413.6916 | 28.9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 42.9 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 113.2 | 28.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 60.9 | 20.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 110.7 | 12.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 24.9 | 8.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39.9 | 13.3 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 65.2 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.5 | 22.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 631.8 | 24.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 782.1283 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 113.2 | 28.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 145.3417 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 46.5 | 9.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 256.2 | 18.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 281.7 | 31.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 297.845 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 81.2 | 20.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 43.1383 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 315.6 | 26.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 782.4 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 45.645 | 15.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 66.9 | 22.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 136.5 | 27.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 69.2 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 86.1 | 12.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 366 | 18.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 723.845 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 28.6 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 85.8 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 97.8 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 121.1 | 17.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 157.0617 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 195.6 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 33.9 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 157.3 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 85.2 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 136.5 | 27.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 48.9 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 146.9 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 537.9 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384.3333 | 20 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 343.9999 | 120 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 35.7 | 5.1 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 10.0833 | 11 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.3867 | 28.16 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 668 | 60 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 311.6665 | 220 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 24.2 | 12.1 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 56 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 313.9 | 4.3 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.939 | 6.18 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3442.8 | 36 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 7.425 | 4.95 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 19.4 | 9.7 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.3666 | 117.22 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.8333 | 70 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5 | 30 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.98 | 55.49 | 1 | 1 | 0105-Bunker structures | D2-Forced - Delayed | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 62 | 20 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 41.8 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 61.3333 | 20 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1006.05 | 57 | 1 | 1 | 0105-Bunker structures | U1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 192 | 40 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 177.6667 | 20 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.9999 | 120 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 881.076 | 55.53 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.295 | 5.18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.45 | 421 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 482.27 | 166.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 985.2 | 246.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 78.75 | 21 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 785.9826 | 137.09 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1822.5 | 225 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.8 | 64 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.9999 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.1388 | 41.63 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3062.5 | 245 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 315 | 105 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 407.05 | 116.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 924.9999 | 277.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2824.2665 | 623 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3200.6833 | 181 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.7832 | 179 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.5 | 165 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 770 | 110 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1370.6332 | 316.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7517.3965 | 316.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.0124 | 92.25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 427.4999 | 135 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 495 | 110 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 571.4998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 966 | 161 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1414.9998 | 300 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.0566 | 127.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1352.5 | 30 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2258.9998 | 540 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.1532 | 124.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.1666 | 145 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2270.438 | 167.56 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 32 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 221.6666 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4101.5832 | 415 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.696 | 45.36 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7269.3328 | 752 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | SF-Startup Failure | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.1083 | 5.18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 391.5 | 270 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1677.5 | 305 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 534.4605 | 169.67 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1574.9394 | 179.31 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1967.45 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2164.1663 | 490 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3419.9998 | 540 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 3.5333 | 4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.7177 | 20.18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.648 | 25.81 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.6 | 28 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 518.1333 | 67 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 712 | 356 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 734.379 | 120.39 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6373.25 | 490.25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5347.95 | 101 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.442 | 6.18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.1807 | 11.72 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.9333 | 124 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 761.862 | 70.11 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 980 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1242.5 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5113.5165 | 316.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 551 | 275.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 800 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 846.0832 | 143 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1975 | 395 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 156.4 | 184 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 702.1 | 351.05 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1099.9999 | 165 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3920.4665 | 542 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5305.4163 | 535 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9653.3328 | 800 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 142.6167 | 19.9 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 800-Miscellaneous
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 836.4999 | 105 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 201.3333 | 80 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 63.15 | 21.05 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 7 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 18.24 | 9.12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.4 | 5.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 15.6 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 3690.5 | 610 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 27.36 | 9.12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 68.115 | 17.1 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 7.5 | 7.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 8 | 8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 56.25 | 37.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 24.375 | 37.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 6 | 6 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 22.65 | 7.55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 16.78 | 8.39 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 14.94 | 4.98 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 30.8 | 4.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 580.39 | 45.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 101.25 | 20.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 5 | 5 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 10.4 | 5.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 29.94 | 9.98 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 15.19 | 15.19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 355.74 | 25.41 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 50 | 10 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 9.93 | 3.31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 6 | 6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 26 | 6.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 4 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 12 | 12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 9.62 | 9.62 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 106.48 | 26.62 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 9.2 | 9.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 56.35 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 119.5833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 22.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 10.8 | 27 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 16.0333 | 37 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 37.0833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 702.1 | 51 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2066.15 | 43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 7.8833 | 43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 69.3 | 27 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 70 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 24.5333 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 137.0833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1221.2667 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 27.0666 | 28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 11.7333 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 75 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 5.3333 | 20 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 5.95 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 5.3333 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 26.6667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 495.4167 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 44.1666 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 187.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 25 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 818.3333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 98.6 | 51 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 50 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 192.0833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 231 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 446.6667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 200 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 2098.3665 | 238 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.2 | 8.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.6 | 8.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 47 | 9.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 72 | 4.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 179.8 | 5.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 47.8333 | 14 | 1 | 1 | 0114-Solid fuel volumetric feeder | D2-Forced - Delayed | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 453.2 | 33 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 40 | 8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 60.5 | 5.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 254.8 | 18.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 20.6 | 10.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 91 | 18.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 98.975 | 10.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28.4 | 7.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 88 | 8.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 14.4 | 7.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 48 | 12 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4.6 | 4.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34.2 | 5.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 50.4 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18.6 | 6.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21.5 | 4.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 59 | 5.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 4 | 4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 25.9 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 55.3 | 7.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 46 | 9.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 65.7 | 21.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 369.2 | 28.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 19 | 9.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.9 | 4.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 17.6 | 4.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 21.2 | 10.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 37.6 | 4.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 19.2 | 4.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 268.3333 | 28 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.4 | 9.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.6 | 4.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16 | 4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 79.3 | 6.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 138.6 | 7.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 106.8217 | 10.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 244.4999 | 90 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 18.2 | 12 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 6335.4349 | 386.7 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 22.5 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 52.5 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 28.35 | 21 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 98.3333 | 20 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 9.2 | 6 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 130.2 | 31 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 117.9 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 101.4 | 52 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 222 | 30 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 322.3 | 33 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3.65 | 3 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | TRE | Off-Peak | 9.9667 | 26 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1536.7 | 12.7 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 162.6 | 27.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 5.5 | 5.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 1463.8185 | 37.39 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 37.51 | 37.51 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 351 | 27 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3.8 | 3.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 165 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 563.75 | 275 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 21.6667 | 10 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 583.814 | 37.91 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 48.15 | 16.05 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 110 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1695.8332 | 370 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 21.78 | 10.89 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 224.25 | 195 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 71.6 | 24 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.1 | 4.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 54.0833 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 388.4165 | 295 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | WECC | Winter | 496.315 | 5.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 37.6833 | 19 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 151.48 | 2.1 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1029.0833 | 53 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68 | 68 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 344.5333 | 68 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1208.6666 | 140 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4252.1999 | 342 | 1 | 1 | 0129-Other coal processing system problems | D3-Forced - Postponed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3150.8725 | 25.05 | 1 | 1 | 0129-Other coal processing system problems | U2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.8 | 144 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 212 | 40 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1439.9996 | 540 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4800 | 300 | 2 | 2 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 98.2667 | 44 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 282.192 | 470.32 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7262.35 | 431 | 1 | 1 | 0129-Other coal processing system problems | U2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 190 | 190 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 759 | 330 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.5666 | 94 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 583.8666 | 151 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.3333 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.4 | 201 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4305 | 205 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 417 | 417 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 719.9998 | 270 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 458.1999 | 87 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4640 | 290 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 161.3333 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 963 | 45 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 360.8 | 48 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1401.75 | 45 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2806.4166 | 85 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1588.6666 | 40 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 123.2666 | 43 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 776.8666 | 43 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 569.5 | 51 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 450 | 45 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0150 | Sorbent feed conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 380 | 20 | 1 | 1 | 0150-Sorbent feed conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 62.65 | 21 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 93 | 31 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 183.8167 | 41 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 494.665 | 12.7 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 346.875 | 3.7 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1240.3 | 79 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1200 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 786.25 | 15 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2270.95 | 41.29 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7849.32 | 52.68 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19644.3333 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.8333 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5345.4375 | 55.25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 492.8 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 528 | 64 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 601.9999 | 84 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 264 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215.6667 | 20 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5272 | 32 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 429.3333 | 32 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 835.0333 | 94 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.2 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 636.8 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1644.8 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1275 | 75 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 49.35 | 47 | 1 | 1 | 0205-Pulverizer exhauster fan drive | U1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 680 | 170 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 581.85 | 81 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2223.9999 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301.75 | 355 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8036.9998 | 270 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 10 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1879.4998 | 315 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 639.5833 | 125 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 848.9999 | 180 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.8 | 63 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 454.3331 | 290 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4825.3328 | 770 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 163.3333 | 70 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2063.9664 | 433 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 240 | 240 | 1 | 1 | 0240-Pulverized coal bin | D3-Forced - Postponed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207.5833 | 235 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 382.5 | 150 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1343.6666 | 145 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4801.4999 | 270 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 346.6666 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.4999 | 210 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3066.2333 | 119 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2938.4999 | 270 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6666 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105 | 150 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 400 | 400 | 1 | 1 | 0240-Pulverized coal bin | D3-Forced - Postponed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 406.333 | 530 | 1 | 1 | 0240-Pulverized coal bin | D3-Forced - Postponed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.2999 | 333 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.6667 | 5 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.25 | 53 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10456.2499 | 375 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.632 | 51.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.0333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.4333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.485 | 44.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.1333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.2333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.415 | 160.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.131 | 84.51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.8 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 162.9166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.3 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.1833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 359.7166 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 390.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 566.4 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 649.9997 | 390 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 719.82 | 133.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 829.35 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 915.3 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1095.33 | 37.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1320 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1334.8 | 284 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1743.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3310.8331 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3540 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3660 | 488 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.7 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.6333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.22 | 61.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 17.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.51 | 185.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.2 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.15 | 100.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.1666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.9666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.5966 | 154.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.4667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 220.1333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 255.2 | 232 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 293.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 421.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 467.1466 | 184.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 479.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 525.1 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 591.6 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 683.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 932.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1255.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1361.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1547.7421 | 74.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1848 | 308 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2518.8333 | 88.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3040 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3575.0499 | 381 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8649.9999 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10751.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.0833 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.728 | 36.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.1167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.465 | 50.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 90 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.9666 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.0666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 123.7666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139.9666 | 110.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 143.0666 | 296 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 167.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168 | 420 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 186.547 | 110.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 301.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 373.45 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 462.1066 | 161.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 473.7333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 541.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 771.2141 | 180.05 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1121.7066 | 210.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1171.5 | 213 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1192.3333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1200 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1245.0532 | 287.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1302 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1389.8332 | 269 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1512.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2268.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 232.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 369.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.2 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.8833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.7333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60.9666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.3666 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 141.6285 | 24.21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 177.0666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 460.632 | 45.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 581.5675 | 98.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.1 | 2.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.11 | 1.81 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.2 | 5.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1665 | 22.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4020.39 | 14.41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2993.41 | 10.43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162 | 20.25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 378 | 108 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 580 | 11.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 355.8333 | 175 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 543.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 600 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.0667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12100.3329 | 620 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 305.235 | 359.1 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1276.8333 | 235 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6779.4996 | 546 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.1666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 51.3666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91.7333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.853 | 70.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.5517 | 180.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.5832 | 325 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 260 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.7 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 294.4999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 327.5742 | 190.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 338.4332 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368.2 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 384 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 388.2666 | 224 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.25 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 467.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 493.8666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 544 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 566.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 597.5833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 615.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 624 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 651.3376 | 125.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 944.768 | 116.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1166.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1183.2983 | 125.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1925.9999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1950 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2060.5541 | 226.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2444.0665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4621.0666 | 344 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.65 | 53 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.9483 | 28.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.65 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.1666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.4 | 100.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.6666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117.5 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.1 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 148.105 | 155.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.5 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 164.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.6667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 206.4 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264.5333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.1 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 319.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 320.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 322.896 | 115.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 339.1999 | 254.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 453.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 536 | 268 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 572.9167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630.7666 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 634.26 | 115.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 655.6 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 678 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 887.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1053.9999 | 204 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1368 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1577.025 | 140.18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2218.8833 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.2717 | 24.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.6666 | 161 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.6999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.7333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 138.75 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.6 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 199.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 266.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 276.2499 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 286 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 288.35 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 293.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 294 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 297.6665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 327.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 342.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 351.8233 | 81.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 391.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 495 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 570.5832 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 622.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 682.4333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 750 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 768.95 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 790.575 | 210.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1017.5 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2926 | 532 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3046.349 | 210.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76582.6 | 775.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 24 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 193.05 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3896.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 52.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 229.7621 | 67.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.3 | 13.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.3333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81.95 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 162.6666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 411.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 479.7 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 993.9475 | 131.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1348.386 | 69.03 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.8 | 78 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260.2666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440.96 | 33.92 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1035 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.5 | 1.75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 154 | 88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1876.7461 | 189.89 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62.7 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.7333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 693.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1313.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 332.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 363.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14047.6664 | 340 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.41667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.8 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.222 | 112.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.7333 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.8265 | 54.23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.1665 | 46.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 36.9 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.2 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.6 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.9333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.95 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.4666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.3333 | 64.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.9166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 152.7333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180.1666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.75 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.25 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 253.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 345.6 | 216 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 402.7998 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 429 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 484.5 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 508.7499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 519.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 627.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 715.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 750.7499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 915 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 937.95 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1191.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1244.889 | 461.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1310 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1319.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1391.8666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1561.35 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1678.147 | 120.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2256 | 282 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3628.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3631.3664 | 394 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3800 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4129.3 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.7666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.0333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.545 | 83.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.3333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.15 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.1833 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.4166 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.9166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.9939 | 104.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.2666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.0999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.45 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 224 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.1998 | 367.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.8 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 321.2 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352.8331 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 357 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 424.926 | 139.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 435.4166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.2666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 476.2666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 505.764 | 187.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 643.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 647.5 | 370 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 648.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 661.4833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 667.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 707.8373 | 123.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 822.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1015 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1070 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1088 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1358.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1671.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3484.8331 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 13.8333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.1375 | 6.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135.0499 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.0333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 141.355 | 166.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 183.0166 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 249.3629 | 145.26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280.364 | 329.84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 370 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 387.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 524.2999 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 794.9332 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1162 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2587.7766 | 97.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4353.3534 | 363.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7670.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37660 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.2833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 348.4998 | 246 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1267.3363 | 78.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.6 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.0333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 587.7333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.8666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 106.6666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 333.2 | 83.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 657.275 | 64.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2556.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 27 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 16.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63 | 12.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 218.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 582.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1161 | 43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 237.6666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 630 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.9166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 300 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 408.9 | 94 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 744.7999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1271.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | U2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.9 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.25 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.5283 | 21.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.1831 | 293 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.3333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.6333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.7 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.5 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.6666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.175 | 52.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 172.5664 | 334 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 179.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 181.2998 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 266.3333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 363 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 477.9166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 714 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 818.5767 | 129.59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 825 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 998.2 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1064 | 266 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1097.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1365.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1506.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1591 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1625 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1926.39 | 141.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1948.3332 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2245 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3246.9225 | 277.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7065.9746 | 310.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.8 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.496 | 68.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.352 | 30.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.5 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 176.85 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 205 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 318 | 318 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 462.28 | 88.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 485.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 556.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 580.9 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 641.6666 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 696.8498 | 231 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 757.1666 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1193.5 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1232.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1240.1457 | 156.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2514.7815 | 217.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2781.25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.8 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.3333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.55 | 39.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.1 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 49.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.2 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.4167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80.6666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105.9519 | 198.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 174.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 178.5 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 212 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 230 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.9559 | 202.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 336 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 366.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 490.8332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 559.5833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 650.9833 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 768.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1156.2499 | 375 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1652 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1876.98 | 130.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2854.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3608 | 328 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3630 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4414.05 | 490.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 250.75 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 587.0666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1672.8048 | 83.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15.7666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 197.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 231.3 | 69.39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1054.1999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.9833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126.1 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 138.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.8 | 22.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 785.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.01 | 20.67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.878 | 66.66 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 141.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 260.01 | 28.89 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.1666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 226.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 331.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 698.5333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1009.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1654 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3500.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 363 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.35 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.9 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.8499 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.6667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.7 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.1667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.0166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.0833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.4166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.2 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163 | 81.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.0333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.1 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 193.6331 | 314 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 226.2 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.5498 | 369 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293 | 293 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 350.4 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 352.7499 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410.2833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 484.2 | 269 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 510 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 535.5333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 553.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 597.6509 | 245.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 616.239 | 61.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 644.0333 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 669.3 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 708.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 715.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 835.9998 | 264 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 837 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 852.7725 | 37.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 890.6666 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 891.0666 | 65.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1404.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1466.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1573.15 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1689.5199 | 181.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1759.3332 | 520 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1808 | 226 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1965.1498 | 297 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2796 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6502.4999 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.7375 | 38.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.2667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.3333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.4 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.6816 | 81.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.735 | 82.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 31 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.8166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 37.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.8833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.5 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.592 | 134.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.7499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.7833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.2333 | 204.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 131.25 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144.15 | 115.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.35 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 204.678 | 49.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 227.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.5666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 263.28 | 219.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 357.6841 | 156.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 374 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 423.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.3333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 550 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 593.7533 | 52.39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 638 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 686 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 822.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1128.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1804.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2747.7 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.0833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.1 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.4166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 19.4666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.6666 | 124 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.2 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.8666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.7866 | 87.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.4166 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.5333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.9166 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.6 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129.0666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135.3666 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 173.2666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 232.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 271.051 | 132.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.2064 | 175.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 390.1331 | 308 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 444.168 | 35.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 459.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 529.2066 | 65.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 563.5 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 599.95 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 647.5416 | 310.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1191.6666 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1880.525 | 175.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3683.9 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.0666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 69 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 185 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 233.6333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 601.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 916.8726 | 63.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.5667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.8047 | 47.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.8 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.8667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.146 | 62.42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.5006 | 52.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.265 | 64.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.0832 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 256.7 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 865 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 46.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.1666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 66.6999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 117.8 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 146.7 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 164.8333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 219.0588 | 56.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 624.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 751.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 47 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.9 | 13.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 909 | 18.18 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1163.9 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.9 | 12.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.1 | 3.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.4568 | 178.03 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 547.2 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1430 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 211.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 266.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 486.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 702 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2268 | 840 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.3866 | 99.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.9333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.2 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.5 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.99 | 46.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.3166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 132.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153.2666 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.9166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 185 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 296 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 342.1998 | 354 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 347.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480.5833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 535 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 579.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 600 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 817.3166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 861.3999 | 354 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 865 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1226.4998 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1423.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1466.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.05 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.2 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.9733 | 74.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.6666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 216 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.7333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 289.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 376.2319 | 172.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 425.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428.48 | 82.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 445.5 | 198 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 472.8666 | 173 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 662.8666 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 665.0333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 886.6665 | 380 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1040 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1331.1 | 261 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1714 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1845 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2832.65 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4900 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.9833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.6666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.3 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.9998 | 360 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.9666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.2499 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76.25 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.7333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 84 | 336 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 118 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.2 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 206.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 247.5 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 367.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 443.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 463.1 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 467 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 471.7386 | 160.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 525 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 612 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 623.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 630 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 734.85 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 816.6639 | 197.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 981.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1173.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2151.75 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2761.352 | 313.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3149.1039 | 208.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3423 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11340 | 420 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.55 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.1 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.5 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 727.6 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 760.2041 | 42.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 847 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1696.9332 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.8333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.25 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.7666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 78.4 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.5166 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 114.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 36.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 121.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 155.944 | 48.48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 171.2966 | 34.84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 249.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 295.36 | 56.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 420 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 632.4 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 525.6667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.2 | 4.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.5 | 11.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 396.8 | 32 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1221.8 | 29.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193 | 386 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 168.3 | 66 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 256.2 | 61 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 545 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1306.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 516.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 175.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 477.9 | 81 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16202.6665 | 620 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1380 | 600 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2844.6664 | 340 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.4166 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.9933 | 35.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.6666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79.7333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85.3999 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.5333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 135.5166 | 173 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141.1332 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.1333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.5 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.245 | 52.07 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 191.9 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.0166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 214.5 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.1665 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.8664 | 448 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.1 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 333.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423.9 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 435.2211 | 99.29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 442.0585 | 188.11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 490 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 524.6 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 640.6666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 663 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 747.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 839.9833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 856.1193 | 89.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 873.95 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 874 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 992.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1048.4625 | 175.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1166.6665 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1283.3331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1426.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2129.4165 | 253 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2478.948 | 148.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7092.1331 | 344 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.435 | 19.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.1333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.1716 | 42.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44.1 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.9999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.8466 | 141.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.6333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.925 | 100.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.3333 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.2666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 165.292 | 115.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 222.7983 | 118.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 282.4666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 292.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 382.0833 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 431.9333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 439.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 456 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 513 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 517.4239 | 106.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 656.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 900.9333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1138.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1322.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1338.5475 | 130.59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1410.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1662 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1710 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1908 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1983.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1995 | 228 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2824.8 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4662.0932 | 210.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113520 | 430 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.55 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.2 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.95 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.8 | 70.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.637 | 117.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133.9333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140.12 | 135.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.35 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 163.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 164.9766 | 115.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 275.1833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 281.7666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 282 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288.35 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 409.764 | 213.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 423.6666 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 486.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 565.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 614.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 659.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1027.5832 | 295 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1068.683 | 138.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1192.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1286.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1596 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2069.6907 | 189.59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2864.6999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5856.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6245.1999 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19998.0687 | 775.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25012.95 | 490.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.3833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.8333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 237.65 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 615.6 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 666.2499 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 873.933 | 94.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.25 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1292.9539 | 86.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 31.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.7666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.6166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 355.05 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 365.15 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 506.25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2634 | 109.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.8 | 7.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 452 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1366.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4127.2 | 30.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.6 | 41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11048.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 198 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3122.25 | 181 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1176.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.85 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5.95 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.1666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 167.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189.5833 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 219.3332 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 280.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 286 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287.8666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 306.1332 | 164 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 322.9999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.6 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 428.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 500.05 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 745.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 918 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 927.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 994.6879 | 196.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1058.1333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1896.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2734.6666 | 293 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6174 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9865.7333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.78333 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.9333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.85 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.3833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.3366 | 129.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.9566 | 111.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115.8266 | 124.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.5333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 183.4379 | 139.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 186 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.4166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 348.75 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 387.5999 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 487.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500.323 | 122.03 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 707.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 873 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 882.36 | 139.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 888.25 | 56.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1030.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1148 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1552.6666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2179.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2521.6639 | 115.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3938 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4404.1665 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6677.4666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.6 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.0833 | 32.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.6499 | 133.56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.9 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.9333 | 196 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.9333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.9333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.7333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159.75 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.5 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.8666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 239.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.15 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 286 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 327.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 332.838 | 184.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 358.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 371.7413 | 121.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 382.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 412.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 583.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 747.5 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 780 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1030.6833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1082.3 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1122.2638 | 235.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1213.9099 | 191.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1835.1786 | 215.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2467.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.2 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.5833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.95 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83.4166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.8666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.8 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.0166 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 68.0166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.1965 | 34.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.6 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200.8933 | 115.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 267.3 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 54.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.418 | 16.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.8 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 127.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 160.362 | 40.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 425.0999 | 78.48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 532.35 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1056.905 | 57.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.07 | 4.53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248 | 31 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 255 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 313.6 | 6.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.97 | 18.33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 319.7816 | 61.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.6 | 112 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1597.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.8667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90.1333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 200 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 428.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1289.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 146.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 106.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 248.7333 | 41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1687.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 660 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.05 | 77 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2743.875 | 677.5 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4710.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 31.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 162.75 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1054.5333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 91.5666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 926.6 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 102 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 457.8666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 563.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 580.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 352 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1227.4 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1067.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 601.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 70 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 45.5 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 16684 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.0166 | 79 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 284 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 452.5 | 90.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1444.5 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.575 | 28.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220 | 44 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 385 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.0417 | 14.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 285 | 285 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230.3 | 94 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.2175 | 46.41 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 96 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 331.5 | 117 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 176.4165 | 365 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2119.8 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.7667 | 26 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 635.6 | 56 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 758.7113 | 62.02 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.0285 | 28.77 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111.6666 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2537.4996 | 609 | 1 | 1 | 0253-Pulverizer feeder motor | SF-Startup Failure | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 216.5833 | 115 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.4666 | 73 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 230.9999 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2303.1 | 81 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 484 | 44 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 219.5066 | 65.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 841.75 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 266.6666 | 160 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16808.3333 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 252.65 | 31 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 271.7 | 66 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 616 | 176 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.635 | 5.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 400 | 80 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 318.75 | 125 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 302.427 | 131.49 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208.3333 | 100 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 125 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.8999 | 219 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214.4849 | 162.9 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102 | 24 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 772.62 | 65.2 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.415 | 47.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.5833 | 95 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 120.48 | 100.4 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 511.9999 | 240 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5288.8333 | 130 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 440.1 | 65.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1072.1 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.9995 | 109.41 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.5833 | 83 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1957.5 | 150 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12674.75 | 605 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 422.2839 | 131.28 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43.4666 | 65.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.8333 | 70 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1075.2933 | 28.1 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 889.3236 | 57.13 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1399.9999 | 210 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 775.75 | 145 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 150 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 215.177 | 120.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 198.1676 | 130.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 296.947 | 100.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.3333 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.7695 | 18.63 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 391.9999 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 675 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 704 | 88 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1331.4167 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1677.3333 | 148 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6996 | 44 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1350 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 160.65 | 357 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4409.5833 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7070 | 140 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.98 | 5.59 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3801.82 | 15.71 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1501 | 190 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 879.1666 | 125 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1123.4166 | 85 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9000 | 750 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1867.4498 | 507 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.445 | 6.89 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 97.9999 | 420 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10596 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.6666 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.2 | 72 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324 | 54 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1575 | 350 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.3333 | 80 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 883.3332 | 265 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.9999 | 90 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11205 | 249 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25798.9331 | 416 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.5333 | 94 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.6667 | 26 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 206.4666 | 65.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.5333 | 65.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1145.4 | 498 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2260 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3765.5831 | 365 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10787 | 460 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 353.8333 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 18628.8664 | 382 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 7.25 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375.02 | 22.06 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65.3332 | 245 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.58 | 65.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.0666 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4884 | 44 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8052 | 44 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9078.2 | 57 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.9166 | 83 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.1333 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 490.5833 | 29 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3482.0831 | 305 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.65 | 73 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1920 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4380.4 | 94 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52584.25 | 145 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121 | 12.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 498 | 12.45 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3504.233 | 503 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 804.76 | 25.96 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.1488 | 13.73 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.0666 | 98 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 710.68 | 65.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 834.9 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1122.1 | 49 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.8333 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268.3333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288.3833 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3853.3328 | 800 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6032.4998 | 570 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10072.9999 | 210 | 1 | 1 | 0260-Primary air fan | U3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.3667 | 26 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1492.4 | 287 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4636.8 | 504 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 223.0999 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 562.0833 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 983.3332 | 200 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31913.8332 | 457 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 60.2333 | 139 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 238 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 126 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.01 | 22.89 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 359.04 | 32.64 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.2 | 29.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.9166 | 145 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1755.6665 | 458 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50595.9995 | 780 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.3333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 46.6666 | 350 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 205.38 | 65.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 284.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8333 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1133.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 716.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1320 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.2 | 14.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.18 | 4.22 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345.1 | 9.86 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80.5 | 115 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 413 | 118 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 547.1666 | 49 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1347.1333 | 121 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18714.3332 | 460 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 364 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 644 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 845.6 | 302 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 993.75 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1092.5 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1601.6 | 132 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18250.8 | 36 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.9167 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 482.9166 | 305 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 925 | 500 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 12593.9999 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 42056.0496 | 537 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 218 | 21.8 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1380.6 | 468 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 321.9999 | 105 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19839.6665 | 530 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1441192.5 | 405 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2700 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91 | 91 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.7533 | 125.32 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2430.3332 | 460 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1930.5 | 234 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7307.5971 | 662.32 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 233.3331 | 350 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 692.9998 | 270 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.25 | 57 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1413.3332 | 400 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1521.5 | 170 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3079.3329 | 620 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7095.55 | 97 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7463.383 | 569 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.5 | 85 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1995 | 95 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1022.6663 | 520 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 732.6666 | 157 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85 | 85 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5470.4164 | 475 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.3333 | 26 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1168.5 | 410 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13208 | 520 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.5 | 13 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5646.6665 | 350 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1215 | 150 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9882.8333 | 43 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68 | 20 | 1 | 2 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 190 | 120 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 450 | 180 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.6666 | 40 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 202.2833 | 53 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 50 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9429.5832 | 265 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8702.833 | 470 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3799.9995 | 750 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1426.25 | 175 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 326.4666 | 118 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6421.9 | 298 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4262.1663 | 535 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 985.8333 | 65 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5066.6666 | 200 | 1 | 1 | 0263-Primary air fan drives | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 315.37 | 28.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2167.9999 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47 | 15 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6769.9998 | 600 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6489 | 9 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 289 | 68 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3603.9998 | 240 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4299.15 | 9 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.2 | 232 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2340 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5003.9999 | 270 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 445.5333 | 65.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1912.4999 | 270 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2499.9999 | 300 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33553.9996 | 570 | 1 | 1 | 0264-Other primary air fan problems | SF-Startup Failure | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 726 | 220 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111.9266 | 65.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 402.4999 | 210 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1097.8333 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1399.9998 | 300 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6210 | 20 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6097.4999 | 270 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7440 | 10 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 511.8667 | 44 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21319.3331 | 565 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.6 | 65.2 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.0499 | 219 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8664.1664 | 370 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11431.2499 | 75 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 621 | 60 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6 | 14 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1018.333 | 470 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.5 | 95 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1387.2832 | 216.2 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15543.6664 | 340 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19250 | 770 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 377.2285 | 182.53 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1460.4651 | 252.53 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 16 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2592 | 20 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 28066.5415 | 642.5 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1306.6665 | 560 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2541.4433 | 146.2 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8112 | 320 | 1 | 1 | 0265-Primary air heater | U3-Forced - Postponed | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.05 | 27 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 396.6667 | 20 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9502.5 | 35 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1060.0333 | 22 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 996.2 | 293 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 121.1346 | 77.32 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.75 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 387.75 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3375.3 | 18 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.6666 | 115 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.3333 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.5666 | 127 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 770.9333 | 56 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1246.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.5 | 41 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.95 | 17 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.6832 | 203 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.2 | 36 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4731.282 | 775.62 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7834.0768 | 750.87 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.25 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 244.8373 | 63.32 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172 | 21.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88 | 32 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1565.6666 | 140 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 64.5 | 43 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 643.1939 | 139.32 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1595 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2029.5 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 708.75 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1787.1493 | 87.32 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.5 | 53 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.6 | 52 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23.7499 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1354.5 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2561.6666 | 145 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 252.8 | 64 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1328 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 680.616 | 49.32 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 15.7667 | 22 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 967.5 | 430 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.6833 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.6833 | 121 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.842 | 77.69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1530 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 840 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1671.75 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 142.2667 | 44 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143.9999 | 270 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1085 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2348.2666 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 264.35 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.6666 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26083.3331 | 625 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12870 | 650 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34528.9491 | 662.32 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18580.1665 | 262 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.95 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3310.4165 | 175 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.9 | 174 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.9 | 44.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 495.8 | 67 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510.75 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1068.9166 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1311.3331 | 281 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 254.8 | 104 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300 | 200 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 996.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1195.3333 | 88 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1275.5499 | 291 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4760.9999 | 270 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.2 | 54 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 505.3333 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2672 | 167 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 254.5833 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6346.1333 | 163 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 240.8 | 301 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 261 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 387.6 | 17 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 799 | 340 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 963.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4299.4665 | 184 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1795.2 | 96 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 728.3449 | 118.11 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35889.1332 | 149 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 535.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 628.9999 | 102 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 727.8666 | 206 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1900 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.1666 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.7495 | 41.17 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 104.1666 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260.8497 | 423 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2870 | 287 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 491.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.8333 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3403.8 | 18 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3894.9997 | 492 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589.05 | 99 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.5833 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.3499 | 177 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181 | 90.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325.3333 | 80 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 634.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 659.575 | 188.45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2079 | 378 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60920.5 | 185 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.3331 | 317 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.75 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 805.4666 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.1999 | 144 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 321.7333 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16481.3166 | 89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17193.0332 | 158 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15096 | 34 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1032 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1140.21 | 11.07 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 247.5 | 33 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1037.4663 | 502 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148892.3328 | 770 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22358.7 | 441 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49953.1163 | 601 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.1 | 23.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6 | 11 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.0667 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14786.1 | 54 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5166 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111.3833 | 163 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2250 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 259.1499 | 213 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 304.8666 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1983.585 | 177.9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2593.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 498.4 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 282.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4379 | 151 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.8433 | 59.8 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 323.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 201.2499 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1463.29 | 35.69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2520.5 | 35.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.5 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 362.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1147.2499 | 195 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2446.353 | 120.51 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6698 | 197 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4665.9833 | 83 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12385.4064 | 700.4 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26898.6664 | 770 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.8499 | 87 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 639.8999 | 243 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7132.392 | 134.32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1452.4166 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278.2 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 354 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.0833 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1366.0333 | 214 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119658 | 770 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20514.8332 | 415 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 23606.3332 | 268 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 650-Fluidized Bed
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5833 | 127 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.6666 | 53 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.3333 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.3999 | 84 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.3333 | 80 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 490 | 175 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46848 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 491.6333 | 86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1537.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1840 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.3333 | 95 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 456.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 387.1 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3196.6666 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3999 | 201 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68.9 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20238.3996 | 546 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.1666 | 43 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.3333 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.0833 | 85 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 802.4333 | 181 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4070.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.2 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 211.0833 | 85 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280.082 | 193.16 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 829.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8091.9997 | 510 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.6499 | 123 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.3333 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1295 | 175 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3965 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.6 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8299.9995 | 750 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.8333 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362.4333 | 83 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32130 | 255 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 361 | 90.25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1114 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2235 | 90 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5058.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2610 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.6667 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 383.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1140 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.958 | 49.86 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.5341 | 126.65 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 301.75 | 355 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 365.5 | 102 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 895.7833 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7371 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.0833 | 5 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2334.9958 | 25.13 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1000 | 120 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1003.3333 | 70 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8247.3 | 11.1 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1984.1033 | 9.1 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 407.4217 | 7.1 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1853.5183 | 12.1 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1448.75 | 95 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.8324 | 186.57 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 60 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678.7559 | 164.88 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1184.544 | 25.92 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 409.5 | 91 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.6866 | 46.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261 | 174 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3366.1833 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8557.1333 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8969.1666 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 233.25 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 612 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2339.05 | 287 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2738.3998 | 252 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30025.7894 | 82.53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2586 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 149.46 | 2.82 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 358.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7260 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.6666 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 592.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8901.3832 | 253 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80 | 48 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.6 | 3.6 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.4667 | 47 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3792 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5423.3332 | 200 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8157.7333 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16602.3 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76.25 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 358.3333 | 125 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1894.05 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1936.75 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13265 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6613.16 | 23.2 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38400 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 463.6666 | 52 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4130.6 | 38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6321.6 | 72 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 512.05 | 57 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 940.8 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.65 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111.8333 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4431.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 172 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.0833 | 37 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 143.4999 | 123 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280 | 160 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 483.1665 | 223 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 610 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2450.25 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6694.3333 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.1833 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.22 | 39.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 172.8333 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5842.1999 | 252 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.3 | 38.7 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945.6 | 39.4 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1349.7 | 40.9 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 888.8499 | 87 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 162.15 | 47 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.249 | 37.38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 582.4 | 224 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 769.3333 | 16 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1096.04 | 99.64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1388 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1625.6 | 50.8 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11108.3333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24750 | 275 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.05 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1650 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9536.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 211.2 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.5 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1205.9666 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13935.5 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 479.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5766.75 | 99 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.5 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1169.35 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3445.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3287.4665 | 184 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 252.9998 | 330 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1242.15 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.3333 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.3666 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 258.7166 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4889.7333 | 124 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121482.9915 | 317.05 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.8 | 42.4 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 242.8333 | 47 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 702.2665 | 184 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.6666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.4166 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.9333 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.5333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.268 | 212.52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 215.6567 | 163.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 377.6 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 402.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.3332 | 355 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 477.4164 | 337 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 532.02 | 88.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 585.2166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 595.1824 | 141.15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678.5833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 684.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1000.5 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1161.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1353.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2748.0832 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2895.1 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4428 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18249 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.6667 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.35 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.2 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.3332 | 298 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.82 | 110.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 311 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 637.45 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1022.8666 | 183.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1078.7 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1363.45 | 48.84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1857.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2512.7666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3380.4165 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3490.6665 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.4333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.6 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.25 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.7333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 114 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.52 | 66.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 369.4666 | 65.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 416.25 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 423.0666 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 702 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760.4166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 765 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1005 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1070.9166 | 90.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2035 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2996.6666 | 290 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3788.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4906.25 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17611.725 | 277.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29096.3375 | 490.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.3333 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.7833 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2153.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 148 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 467.2333 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2994.0666 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5295.6166 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 236.5 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3739.8 | 16.26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1642.2667 | 22.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.1 | 7.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 567 | 7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1612.608 | 108.96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.65 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130.3333 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 425.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 782.1 | 66 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1335.35 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.6 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 201.0833 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1055.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 720 | 80 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 433.1998 | 342 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 531.25 | 85 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3926.9998 | 630 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.1695 | 210.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.498 | 133.46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 252.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 252.5 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 263.2667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 296.0333 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 417.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 496 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 546 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 745.5 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 843.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 941.9166 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 990.7333 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1488.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2298.25 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3109.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3222.7999 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4239.6666 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6446.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15813.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 146.6666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.4 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.7166 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.5 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 236.01 | 78.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 338 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 355.6 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 418 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 558.9666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 576 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 619.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 918.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2573 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3629.8166 | 143 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.8 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 274.2666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 335.1333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 423.3 | 166 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477.75 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 547.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 584.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1769 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5747.348 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 407644.3333 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.4833 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.3 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.15 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 144.4 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 249.6 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1867.4333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5955.8333 | 175 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10502.1735 | 147.33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 655.96 | 7.13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1350.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 447.3 | 49.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.4999 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 300 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28696.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.8667 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 553.9 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.4667 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.7666 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 232.3 | 69 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 821.1 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 208.4666 | 53 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 775 | 30 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.805 | 183.22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.9941 | 55.63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 79 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.1666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.984 | 160.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 253.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.5 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 297 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 326 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 351 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 464.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 474.5692 | 273.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 494.4 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 534.0832 | 221 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 628.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 646 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 740.647 | 110.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 795 | 318 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 837.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1093.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1103.9 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1167.1666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1431.392 | 130.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1667.25 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1815 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3637.1666 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3948.0999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6647.7133 | 34.12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11711.744 | 166.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.4166 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.0833 | 88.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.3332 | 283 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.0659 | 181.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250.2 | 55.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 288 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 339.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 359.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 406.25 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 450 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 463.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 463.3546 | 267.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 570.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 704 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 850.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 936.7166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1127 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1280.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1335.9165 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1564 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1722 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1956 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2295 | 153 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2297.26 | 73.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2553.95 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4712.5 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6875 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9277.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.2 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.3499 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 186.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 189.2 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 206.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 246.6783 | 166.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 260.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 284.7949 | 216.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 312 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 318.5833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 504 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 526.9 | 263.45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 826.6666 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1116 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1118 | 215 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1270 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1533.4665 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1841.2965 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1899.2166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1899.8906 | 210.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3465 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11805.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36610.2 | 277.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.3333 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 208.1333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 582.6332 | 454 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.4666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1334.4166 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1096.4165 | 223 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2306.1333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 742.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1619.2 | 10.12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 825.21 | 15.57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 624.4166 | 127 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2484.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2816.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5512 | 265 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.4333 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.45 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.9166 | 175 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 368.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 424.15 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 861.6833 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5475 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1035.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4303 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9800 | 280 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1129.3333 | 77 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18.6666 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.2698 | 92.59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.4 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.7333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110.84 | 65.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.05 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 383.25 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 519.0666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 617.5666 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 661.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 814.5241 | 264.17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 864.9037 | 378.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 865.7831 | 287 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 937.6666 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1144.9835 | 65.49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1189 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2145 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2560.5999 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2838.473 | 160.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3689.5833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4170.1 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11736.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19840 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11.4833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.5833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.7333 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91.4666 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.1666 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217.6 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 253.7333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 286 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 344 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392.7 | 231 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 637.89 | 77.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 774.5333 | 157 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 869.25 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1142.1665 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1293.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1397.5166 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1909.3666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4338 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.0356 | 137.71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86.4 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 101.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.4 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.7833 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.775 | 66.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 290.72 | 63.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 341.25 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 378 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 408 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 532.4666 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 794.2666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1580 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1656.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3003.08 | 750.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4702.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9961.3264 | 755.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62455.2499 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.4833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 236.8833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1460.1 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 446.4666 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 299.3 | 4.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.8 | 41.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1150.3333 | 145 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1703.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2328.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.3332 | 170 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.2 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 190.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 253 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 292.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 713.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 908.1333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 455.4666 | 122 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3936.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 201.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 213.3 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 436.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1285.4666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 674.5 | 57 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 56.1 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 161.5 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.2 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240.2166 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 360 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 370.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 617.4 | 294 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632.0249 | 143.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 867 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 875 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 951.9999 | 168 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1087.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1161.7011 | 300.44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1421 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3139.5 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4566.3331 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5100 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.3331 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 96.5 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.1666 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153.2667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169.4 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 355 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 409.5391 | 114.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 456 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 544 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 550.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 583.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 625 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 630.3333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 959.9998 | 360 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1458.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1642.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7697.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.6333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.4 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.95 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 146.5333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 178.2133 | 65.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300.6666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.1892 | 206.72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 326.4 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 402.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 726.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1822.2141 | 159.61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2264.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2847.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3712 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4690.7325 | 191.85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5224.2215 | 316.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8771 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2241.4 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3606 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75.726 | 54.09 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 286.1333 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.5333 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118 | 23.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.03 | 65.24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 906.5613 | 43.76 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 936 | 117 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5540.8499 | 189 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6509.7025 | 128.27 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 335.2635 | 46.89 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2715.39 | 201.14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.15 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 707.6 | 122 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1561.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1824.9 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3080.5 | 61 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.1333 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125 | 250 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 344.85 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 289.0666 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 333.4499 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 536.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2800 | 280 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 501 | 15 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23086.9328 | 773 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.1 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 34.2 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.6 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.5832 | 179 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.7333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.0666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.6666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.132 | 180.13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 264.6 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.8 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 332 | 166 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 403.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 429.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 609 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 692.9998 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 734.9333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 797.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 805 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 934.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2007.1332 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2645 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3185 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3504.5999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.5833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.0666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.8166 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.6332 | 206 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.8666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 219.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.4666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273.24 | 22.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 294.9999 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 315 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 360.0135 | 114.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 485.7666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 514.5 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 588 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 602 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 888.5667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 964.7017 | 261.91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1017.75 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1125 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1488 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2023.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2040 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2693.25 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5136.7158 | 51.41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5759.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9806.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15508.5 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15992.9 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.2 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 238.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 332 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 849.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 883.2249 | 216.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1079.1 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2029.8999 | 159 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 284.5333 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 779.3167 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 817.2666 | 299 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1697.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.55 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1200.4667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5463.64 | 45.03 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2551.0041 | 146.75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.1 | 5.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392 | 49 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.965 | 61.74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.1666 | 170 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.0333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 509.8332 | 230 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10304.0832 | 265 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.1667 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.0833 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.5999 | 114 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 301.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1155.7 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5197.5 | 165 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 701.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9063.6 | 166 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2518.1666 | 290 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3402 | 36 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3974.6333 | 59 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1550.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275.4998 | 285 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.4333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.8667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.6986 | 31.36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55.4166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.4667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115.4833 | 169 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.3 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.3331 | 275 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 225.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 310.2 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 358.9666 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 373.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 480.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540.8499 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 631.5832 | 143 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1162.0333 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1650 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2269.2 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4871.3915 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6950.1042 | 160.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16433.425 | 490.55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17251.25 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21583 | 226 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.2 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 13.3338 | 114.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 124.5833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.45 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 342.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 498 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 575.8831 | 317 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1422 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3005.7499 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3339.6666 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53261.75 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.0333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.3332 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.3333 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.35 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 56.6666 | 136 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 182 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 277.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300.8 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 399 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 482.2333 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 603.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1385.4415 | 536.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1545.4833 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2293.4066 | 149.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2385.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2683.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3303.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3493.6666 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4440 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12410 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.2 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 152.1 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2257.8332 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.2 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 269.3333 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 522.5666 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 531.1 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1825 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3501 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8176 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 752 | 37.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2786.04 | 39.24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 525 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 302.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 479.1666 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 731.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1082.2499 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.4 | 18 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.2333 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13834.9999 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 104 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 108.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2090 | 190 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2100 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2133.25 | 23 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7213.2664 | 812 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.6666 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.4999 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 59 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169.4 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 371.8 | 169 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 419.3382 | 282.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 534.75 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 901.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1045.5682 | 139.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1380 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1421.0563 | 353.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1433.8 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1796.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1981.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2090.2665 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2165.3333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2704.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2739.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2835.8333 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17029 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22642.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36200 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.5666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.0191 | 138.89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 94 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114.75 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.5666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.8 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 207.7166 | 121 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 217.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 253.1666 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.25 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 320 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 461.4999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 515.2 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 541.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576.1999 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 582.2512 | 133.34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 876.9 | 29.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1542.15 | 67.05 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3154.8 | 210.32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6780.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6925.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30343.75 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.05 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.8 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 42.7 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.266 | 64.26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 351.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 465 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 714 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1040 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2393.2333 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2861.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3062.8333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4269.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12746.5 | 490.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16792.173 | 775.62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26039.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28990.1983 | 776.87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.1333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 370.3 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 928.2 | 221 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2311.9 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.2666 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 781.2 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64.5833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 275.5 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 504.4 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 313.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.6666 | 209 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.9995 | 271.11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 406.78 | 56.76 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1679.7109 | 162.03 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1733.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 314.535 | 161.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 478.4666 | 143.54 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 507.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 295.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 482.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 900 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3371.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4921.3 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.2 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.6 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 118.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 183.3332 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 579.6666 | 185 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3076.25 | 69 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 742 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4064.2166 | 53 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 719.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 119 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 422.1666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 67.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 49.1666 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 21872.2166 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1830 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 13244 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 80 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.7 | 26 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.2166 | 49 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 974.65 | 101 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 558.6 | 114 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1572.0833 | 175 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.5 | 30 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2521.6666 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6045.1666 | 166 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5 | 110 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.6983 | 86.9 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.5 | 23 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 546 | 28 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 812 | 116 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1132.3 | 67 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.9 | 33 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 239.9833 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 530.1 | 38 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2916.5 | 114 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19135.6595 | 775.77 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.5833 | 25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 234.5652 | 125.66 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 413 | 118 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2495.05 | 139 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 119.1666 | 130 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.5333 | 56 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.5166 | 101 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.4999 | 75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110 | 88 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184.8666 | 236 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17290 | 70 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43287.6555 | 750.87 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2378.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.5 | 77 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 339.5833 | 125 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 666 | 90 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 622.5333 | 92 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5566.6666 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1002 | 90 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 649.74 | 123.76 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 626.9999 | 90 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1599.5666 | 94 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.45 | 9 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.01 | 63.67 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.1 | 14 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 91.2 | 24 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.8 | 106 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 399.9999 | 192 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73.2667 | 14 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.3333 | 4 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.3 | 9 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.2667 | 14 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1117.6666 | 140 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.8333 | 14 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.4 | 36 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.4667 | 4 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 253.2666 | 131 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.4499 | 363 | 1 | 1 | 0315-Pulverizer mill coal level controls | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.6666 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.75 | 111 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238.4666 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260.0666 | 94 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.7 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.1541 | 80.45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.8433 | 85.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.5832 | 253 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.4667 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 490.5 | 218 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66 | 36 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.25 | 5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.6666 | 176 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325.3333 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 631.21 | 7.99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.75 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.2166 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.2999 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.3333 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49603.125 | 277.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 552.5 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.85 | 67 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.8333 | 181 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 433.6767 | 28.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 514 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1602.7 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 292.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.5833 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.75 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 286.2833 | 17.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.1666 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.6 | 67 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 243 | 243 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.2 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 99.4582 | 542.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5095.75 | 65.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81 | 20.25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 375 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.9166 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.9 | 82 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.8999 | 81 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.77 | 41.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30.1 | 86 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94.9999 | 75 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.12 | 85.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.3332 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8022.5 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 197.2425 | 46.41 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 364.2566 | 65.24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156.75 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1194.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 157.5 | 9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 258 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2071.3932 | 317.05 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.25 | 72.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 289 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 654 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1127 | 92 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1289.75 | 105 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.6 | 33.4 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.5666 | 62 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 744 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.6699 | 116.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2314 | 130 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25 | 5 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 996.6666 | 100 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.3333 | 80 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1680.3333 | 71 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 216.3333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 940.3333 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.8666 | 55.6 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 283.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.8666 | 142 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126.5 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.1 | 57 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.9 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.6667 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 606.7666 | 218 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 768 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 495 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2585.5833 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.2 | 56 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 725 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 787.8 | 13 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.4166 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 114.3667 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105.0332 | 137 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 239.4 | 57 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 827.7499 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1384.1666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 612.3333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1071.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4994.8333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.25 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.02 | 12.86 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105.9 | 35.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 843.3333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.9999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 178 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.5666 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 537.3332 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.2 | 194 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 318 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 712.5 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.75 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 444.8 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1255.9999 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2566 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185.6 | 128 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 283.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 520 | 208 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.1126 | 128.84 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141.1666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 202.9999 | 84 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 231.75 | 103 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 800 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.15 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.25 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 387.35 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 200 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2041 | 157 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.5999 | 84 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 354.6666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 787.1999 | 144 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 323.5166 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 924.434 | 377.32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4190.3333 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 695 | 278 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.8 | 25.7 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 12.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.9166 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.9999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 235.1833 | 103 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 541.6666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.5 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 153 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 483.3333 | 125 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.3333 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.5 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 538 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 780 | 240 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 933.2264 | 349.96 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1152.6666 | 91 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1195.3333 | 163 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 166.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175.2 | 72 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.3333 | 148 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4788.9098 | 277.35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.25 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 352 | 120 | 2 | 2 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576.5666 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2924 | 172 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.5833 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 302.142 | 163.32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 550.96 | 29.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1644.5 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.4999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.8333 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 182.9 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 249.0333 | 62 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 253.4999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 260 | 52 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 187.2 | 52 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.6666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.25 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.75 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 812.25 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3304.6 | 124 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 206.9999 | 108 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4973.75 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12060 | 180 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 562.8333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.5 | 7.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 103.5 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.5 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 539.75 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1367.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242.55 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.1667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1217.92 | 76.12 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 341.6 | 122 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.0833 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2685 | 300 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.5 | 54 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 259.35 | 63 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 291.8333 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 375 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 381.5833 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 660 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284.2 | 28 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.9999 | 192 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 460 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.4 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40.5 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4233 | 170 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 42.1666 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 204.1666 | 98 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 571.5833 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.4999 | 150 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 247.25 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3190 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1336 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2273.3 | 179 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2342.3 | 397 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.9 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 600.6 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 834.1332 | 128 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18590.2238 | 775.67 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.5 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 184.5 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 251.75 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.0666 | 88.4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.8 | 182 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 499.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27 | 27 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41.6 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.9333 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 126.3 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 810 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3336.25 | 157 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10657.5 | 145 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.5 | 22 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293.8333 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 514.9998 | 300 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 626.63 | 84.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 933.3331 | 320 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 182 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.5 | 250 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 613.05 | 183 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.25 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 312.5 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 135.15 | 53 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 821.6666 | 34 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1211.6999 | 126 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 40 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6.7833 | 37 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 598.5 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 532.28 | 38.02 | 2 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 684.25 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 211.4666 | 61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 212.85 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 235.4833 | 71 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.75 | 91 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 867.1666 | 121 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.9 | 3.74 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141.8333 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 229.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 534.0833 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 249.0833 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119.1666 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.8 | 138 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.01 | 53.67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10474.6365 | 750.87 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 261.3333 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 228.8 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284.1666 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330.2 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 340.5999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1081.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1185.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4425 | 750 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 347.2 | 56 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144.9 | 42 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287 | 14.35 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.12 | 21.56 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.7383 | 17.9 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 555.3332 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2053.5946 | 150.08 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2249.1 | 441 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.3333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 262 | 131 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306.4826 | 49.97 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1060 | 530 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.2332 | 218 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.4333 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 543.2666 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 690 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2395.2 | 144 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5507 | 7.24 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.8332 | 131 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1695.6 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.0833 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2125.9666 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 337.5 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 408.8333 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.5833 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 882.5833 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 401.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 272.9166 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 11.4333 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 307.45 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 616.3623 | 754.73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 818.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1037.9 | 194 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 606 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 776.5332 | 128 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.1333 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2504.25 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 187.7333 | 32 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153.76 | 9.61 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 154.8666 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 538.65 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 98.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 796 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 840.75 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.3333 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198.75 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 258.5 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.5 | 127 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 490.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 809.5833 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 960 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.7333 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211.6666 | 127 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1127 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 103.1333 | 91 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 259.2 | 81 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 522.1332 | 176 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 559.65 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4671.5833 | 61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 770 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 792 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141.6666 | 34 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 188.1 | 54 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15.3 | 27 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.9167 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.4167 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98.3333 | 118 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 354 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 546.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1908 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.25 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 523.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3800.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16753.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 347.2 | 124 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 358.7666 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 429 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 501.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 560 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 232.2666 | 67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 416.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1258.6 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93.1666 | 86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.5 | 151 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 795.0833 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5609.9999 | 180 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.85 | 21 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1849.5 | 164.4 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.9166 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1616.25 | 431 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.5 | 34 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 281.75 | 245 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1859 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 498 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 682.5 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371 | 106 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2961.9865 | 147.73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88.8166 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1111 | 202 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4488 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2616.5332 | 176 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.25 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 535.7266 | 65.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.3333 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 355 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 380.4666 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 385.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 235.4166 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1327.5 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234 | 195 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3654.5166 | 101 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4666 | 68 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 345 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 27 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 654.8666 | 94 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18705 | 43 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.4 | 127 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.6166 | 109 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 422.4999 | 150 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2976 | 96 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5751.6666 | 145 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381 | 38.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 244.2 | 111 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 306 | 34 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6666 | 125 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500.5 | 182 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 197.5 | 79 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111.8333 | 55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.25 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 610.1667 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 845.75 | 199 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 850 | 200 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 459.1667 | 29 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48 | 36 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 613.3333 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 387.5 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 460.2466 | 89.08 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 744.8 | 114 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 971.6666 | 275 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1012.2665 | 292 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3365.4066 | 65.2 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 418.5331 | 344 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 28.9333 | 31 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Summer | 49.75 | 19.9 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 800-Miscellaneous
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Summer | 79.6 | 19.9 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 800-Miscellaneous
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Summer | 9.95 | 19.9 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 800-Miscellaneous
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1230.9 | 41.03 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6326.2933 | 37.36 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 473.2 | 52 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 389.5 | 41 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 36.522 | 182.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.6 | 66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.75 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.8 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 231.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 594 | 198 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1161.1 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1431.4 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2900 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4248 | 288 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6900.6665 | 440 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 962.5 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6088.3666 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 572 | 208 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 643.75 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 869 | 158 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 968 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1719.6667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1817.0166 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2187.5866 | 85.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2470.4166 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4037.3 | 85.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4043 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5361.9166 | 185 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5889 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 730 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 840.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5300.1664 | 770 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117.1667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 226.8 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260.3333 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 354.9866 | 83.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 439.6333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 493.4997 | 423 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 695.94 | 33.14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1266.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1773.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4179 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6411.3333 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6421.6485 | 751.07 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 38 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 163.3191 | 85.21 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 183.848 | 82.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 193.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 644 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1020 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3745.8333 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14805.75 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47 | 47 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.5 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 147.132 | 122.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.25 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 222.314 | 153.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 247.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 277.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 279.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 381.2666 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 388 | 388 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 736.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 875 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 888.3332 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 999.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1280.75 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2220.8165 | 587 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2904 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3611.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 785 | 100 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 290.4 | 48 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3830.4831 | 739 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 77.4 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.4165 | 455 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.2 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 266.75 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324.3 | 138 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1381.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2844.324 | 338.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6360 | 318 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10975.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29192.75 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 448 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1728.8333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6917.3999 | 170.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 18.8417 | 22.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 479.9666 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 516.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1866.8166 | 101 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4404.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18411 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 922.35 | 129 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 27.3915 | 182.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 140.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182.4 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.125 | 88.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 528.7 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1040.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2603.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4378.05 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15505.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.6 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 122.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.4999 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 299 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 797.7666 | 263 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1573.3333 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 217.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 296.8666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 364 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 589.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 722.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1723.3332 | 188 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2008.7333 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2752.75 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4536.1999 | 111 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 742.5166 | 299 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3187.0997 | 471 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 654.5 | 238 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131 | 65.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.5 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 198 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 296.1623 | 132.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.3332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 608.3 | 158 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 763 | 218 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1074.6666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3047.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.2333 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 143.8833 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158.3999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 243.2 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 294 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.4547 | 22.96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 370.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2016.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2779.1666 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5280 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9738.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 326.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 336.4666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 592.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1091.6665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2043.6166 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14612 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 639.8333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2333.3332 | 140 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 333.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4270.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6163.7328 | 728 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3456.6 | 823 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.1 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.8 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119.4666 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.65 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 266.7559 | 163.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 663.1905 | 382.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 676 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 865.8 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1317.5 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2116.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7579.4166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.9666 | 109 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 612.0833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 985.9998 | 255 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2049.8333 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2226.4999 | 366 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4675 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8364 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.05 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.5549 | 198.66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.5 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.7499 | 82.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.0683 | 60.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 533.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 710.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 800.7 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8989.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.25 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 168.5833 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.8 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 329.9998 | 450 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1554.85 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2778 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3150.2332 | 161 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3264 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7671.3333 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12163.5 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 16.4666 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 464.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 775 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 816.5 | 35.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7453.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.1666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 108.185 | 28.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168.4666 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 219.5833 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 429.55 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 516.885 | 40.54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 964.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1115.5666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1912 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2021 | 188 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 23.25 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 600 | 150 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5736.8998 | 234 | 1 | 1 | 0340-Other pulverizer problems | U2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.0832 | 355 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.5667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121.9333 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.35 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 269.5 | 147 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.8 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 444 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 934 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1280.9166 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2679 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3157.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4849.5 | 318 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17719.2 | 138 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.1665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 351.4165 | 132.61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1903.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12754.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.0333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56 | 56 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.1 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81.5999 | 153 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135.9998 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 277.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 289 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 380 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 380.8166 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 395.8333 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 430.6666 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 736.9166 | 185 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 962.34 | 25.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1481.25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2699.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6468.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1700 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 20 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 29.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 100 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 414 | 72 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 298.8333 | 65.2 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177 | 45 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25953.2934 | 776.27 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 267.162 | 127.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 286.245 | 127.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3390.5257 | 750.67 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3702.102 | 127.22 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.5 | 45 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 935.25 | 45 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1664.6666 | 110 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525 | 35 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.8333 | 70 | 1 | 1 | 0342-Pulverizer inert system | D3-Forced - Postponed | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320 | 50 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3472 | 31 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 332.9999 | 135 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3015.4666 | 176 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 585 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 460 | 115 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 703.9666 | 98 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6577.0833 | 175 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 996.3333 | 28 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.8333 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.6666 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 909.9 | 30.33 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.6367 | 28.1 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.4999 | 135 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 442.6666 | 83 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1312.5833 | 95 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 754 | 120 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3025 | 275 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8033 | 116 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 583.1 | 98 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 380 | 95 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300.2017 | 28.1 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 408.3333 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1592.5 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.3683 | 85.9 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 190.1 | 38.02 | 2 | 2 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.12 | 17.52 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1704.78 | 31.57 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175.98 | 12.57 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10212.5 | 95 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 279 | 62 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144.248 | 9.12 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 475.4165 | 175 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 626.3667 | 38 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.5 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1937.25 | 105 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3162.5 | 275 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34784.5833 | 31 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 736.6666 | 170 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.3333 | 125 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 725 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1429.3333 | 80 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 42 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3948.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1571.1966 | 46.6 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2583.9999 | 255 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43550 | 65 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3789.5833 | 125 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 570.85 | 23.3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 603.75 | 115 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2779.1666 | 290 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44 | 88 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34970 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.5 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 106.3333 | 44 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 135.9998 | 240 | 1 | 2 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 539.75 | 85 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5603.9999 | 180 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16796.6666 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 135 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.6666 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7160 | 80 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 555.9998 | 240 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4219.65 | 27 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6850.25 | 53 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9947.5 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 364.1666 | 115 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 967.5 | 90 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7257.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2872.8 | 18.9 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.3673 | 59.48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.9166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308.1 | 158 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 496.155 | 64.02 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 228.25 | 83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1944.8333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.3166 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.6333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 457.8333 | 82 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.6665 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 159.2499 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 161.1 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 97.75 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177.8949 | 113.55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 671 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1073.25 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 163.1666 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2388 | 240 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 485.6333 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59 | 11.8 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.54 | 55.77 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173 | 34.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.2 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.65 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128.8166 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.45 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.0666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 249.7666 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.4166 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.8833 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 180.2 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 894.1666 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.1 | 89 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.8333 | 25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2880 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282.9167 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1063.3333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1276.1665 | 190 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.3333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.1 | 27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 264.65 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 318.2166 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 409.2 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.25 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 140.6 | 76 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 432.5 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.4666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2906.4 | 144 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8815.3333 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 277.6602 | 177.23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 488.61 | 160.2 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 815.4666 | 176 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 490.8333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 62.0666 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 360.6333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55.0666 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.6166 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.1666 | 67 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1105 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2494.7 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.7499 | 195 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1875 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.25 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.4667 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 321 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 472 | 160 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.5 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84 | 84 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 301 | 84 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.4 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105.45 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 175.35 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 723.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.3333 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 735 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1215.7833 | 61.3 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 151.9999 | 285 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217.555 | 167.35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1080 | 180 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9008.8666 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.4666 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.5 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 233.5333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.0833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 389.8666 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55.8 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 179.9166 | 127 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3566.7075 | 128.53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.15 | 193 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 586.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.232 | 37.92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 224.7 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 501.8 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 820.1565 | 107.21 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 880 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.35 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.7333 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.85 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.55 | 33 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.0833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 162.6666 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 516.25 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 109.0833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1772.4999 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157.6667 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 485.3333 | 112 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 666 | 148 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1287.9 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4166 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.25 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.1833 | 54.92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 688.3332 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.5326 | 280.52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155.8332 | 170 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 217.3333 | 65.2 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 278.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.4 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 164.2666 | 77 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.5666 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.5166 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 239.7333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220.289 | 51.23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.1166 | 127 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.25 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.4499 | 99 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.8333 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.84 | 62.16 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 582.5 | 233 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74698.6666 | 128 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 511.3333 | 118 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 118.35 | 9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 703.4166 | 115 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 869.3333 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1539.2333 | 122 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 10.1333 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.2433 | 55.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 41.3333 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.05 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.6 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 198 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 252 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.5 | 7 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.5 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 556.6666 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1172.149 | 138.99 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3752.5 | 475 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.8803 | 13.57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.3333 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1995 | 76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3661.6 | 184 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187 | 170 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322.6666 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 398.75 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 456.1666 | 85 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 117.3333 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 690.6667 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 541.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.4666 | 73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 359.8333 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1851.7998 | 282 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.5 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.3666 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 615.8666 | 248 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.25 | 115 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290.319 | 200.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 450.4166 | 115 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 899.2666 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15960 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1838.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 51.9999 | 78 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28580 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 99.3333 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1497.4167 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.8 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.4666 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 291.2 | 208 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 752 | 188 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 893 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 295.8 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 573.5 | 37 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1320 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.6667 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.5466 | 137.12 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262.8333 | 166 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.0666 | 148 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.6 | 88 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5150.25 | 21 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 14.3333 | 86 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1354.57 | 36.61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 691.915 | 52.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 676.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.75 | 125 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.6832 | 149.9 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1432 | 160 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 653.3332 | 200 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2159.1667 | 50 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 633.7332 | 194 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 55.4666 | 64 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32.0666 | 52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 96.8999 | 342 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 205.3332 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 562.4683 | 120.1 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 427.2664 | 442 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 330.433 | 431 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 706.2 | 107 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 17.0666 | 64 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1275.75 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 97.3332 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 474 | 24 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2433.6 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 113.95 | 129 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1901.25 | 169 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2862.6665 | 380 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11436.5333 | 104 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3146.5 | 58 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.87 | 64.38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2488.2 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 434.1332 | 352 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11479.3 | 434 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 199.9999 | 120 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7302.15 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1634.1499 | 147 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 228 | 19 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9481.7499 | 345 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8720.4 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 101.3333 | 95 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 485.7667 | 38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10029.1499 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.1 | 93 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 66.6666 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 72.8333 | 19 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 423 | 18 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57873.4994 | 849 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.6999 | 111 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49.95 | 111 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 192.5333 | 38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 49.4666 | 106 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 870.1333 | 104 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1416.7332 | 538 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1350 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 24.6664 | 370 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 44.2164 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3287 | 346 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 737.9666 | 169 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 486.4 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 271.6164 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 53.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1531.8 | 69 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 120.3333 | 38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 452.2665 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 840.9333 | 68 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 182.78 | 24.7 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2363.1833 | 169 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 15443.1332 | 412 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122.6666 | 92 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 215 | 43 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 758.2499 | 135 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 11013.45 | 51 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2295.7999 | 156 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2400.3499 | 183 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 28.5333 | 107 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 819.4499 | 81 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 397.25 | 105 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 650-Fluidized Bed
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 6742.633 | 518 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 90.4167 | 21.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 118.6667 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 333.4664 | 328 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 41.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 87.5 | 42 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 50.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4875 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 903.3916 | 40.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 296 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 614.1333 | 196 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 959.9999 | 288 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 94.1033 | 10.36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3153.5 | 238 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 13.2953 | 10.36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 33 | 33 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 992 | 248 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 213.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 106 | 106 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 154 | 154 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 825.4166 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 55 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 172.3333 | 94 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 3.724 | 37.24 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 860.4166 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1823.72 | 38.1 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 85.5 | 38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 189.3033 | 37.24 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 9507.22 | 38.1 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 272.8 | 176 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 70 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Winter | 40.8333 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 59.1675 | 30.87 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 125 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 866 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 219.8 | 21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 133.1666 | 170 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 2.0833 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 184.45 | 119 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 33748.75 | 95 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Winter | 11.55 | 63 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 4.1 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 232.56 | 12.92 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 752.6983 | 43.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 133.45 | 3.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 13.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 17.9167 | 8.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 503 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1.5867 | 6.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 24.5 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 15.75 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 62.6667 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 142.5 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 7.3333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 81.844 | 29.23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 94.9667 | 14.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6 | 18 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 117.3333 | 64 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 43.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 120 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 9.4783 | 4.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 164.7029 | 159.39 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 30.1 | 86 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 173.5667 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 177.65 | 51 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 4.9833 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.5758 | 30.91 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 26.2833 | 19 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 35.2 | 66 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 102.0833 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 124.8483 | 43.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 318.75 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 905.1782 | 143.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 996.6667 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1656 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 736.6666 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3.63 | 6.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 133.9333 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 216 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 193.3333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 6.02 | 12.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 39.38 | 17.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 92.25 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 550.8 | 51 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 4.6305 | 30.87 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 116.25 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 21.45 | 19.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 289.619 | 13.98 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 159 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 39.6 | 44 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 862-CoG steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 48 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 862-CoG steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 205.8 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 862-CoG steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.0333 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1256.9333 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17855.6 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 270 | 135 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5361 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284.06 | 20.29 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17763.3 | 486 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17304 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8.3333 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4021.25 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 215.7833 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2041.2332 | 209 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2472.9166 | 125 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 40.6333 | 46 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.5 | 110 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8425.92 | 21.44 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10460.4932 | 416.2 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 68.85 | 81 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7738.3333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 151.8667 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 45729.8333 | 19 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6511.9993 | 1110 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28.455 | 27.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9141.6666 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 33.5 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.6 | 116 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 341.88 | 4.62 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54 | 18 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 396.9 | 8.1 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 820.8 | 10.26 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 25928.6667 | 10 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 941.6666 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2948.1666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 130.1667 | 17.75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23.75 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115 | 4.6 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 122.85 | 27 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 674.25 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5543.2 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 405 | 162 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 29.1667 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2483.968 | 14.88 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.1 | 2.86 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1500 | 500 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51 | 68 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17593.3333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3777.3333 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 28770 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1935.2 | 24.19 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 31.5 | 27 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 6529.3831 | 347 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 12661.0666 | 79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 4662 | 252 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 106988.2665 | 416 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 120.9 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 156.25 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1058.4 | 196 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 22.9333 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 509.6 | 196 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 141 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 40.3333 | 96.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 124.9165 | 299.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 41.7999 | 132 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 18.3027 | 10.36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 241.5583 | 70.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 315 | 42 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 18.3733 | 20.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 125.02 | 56.4 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5484.7333 | 196 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13.1 | 26.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4351.4166 | 55 | 1 | 1 | 0360-Burners | U3-Forced - Postponed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 456.4 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 536.2 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 17362.4 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 240 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 11.04 | 44.16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 950.4 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 9870 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 14.504 | 54.39 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 16.36 | 49.08 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 43.6117 | 19.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 461.3 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 256.6666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2.439 | 24.39 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 136.476 | 53.52 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 145.2 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 100.75 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 244.3833 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 328 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 4.4 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 11.7333 | 88 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 243.6 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 2584.4 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 18397.75 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 3594 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 7808.85 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 10161.6 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 80.6333 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 949.025 | 101.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1.2195 | 24.39 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 142.2666 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 13.8 | 69 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 530.8333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2348.2667 | 32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 7.75 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 281.6 | 128 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 21.4 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 42.7411 | 88.43 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 452.2 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 40.3755 | 24.47 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1098 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 148.6653 | 103.72 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 45 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 11 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 3.5333 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 23.2125 | 55.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 2487.2333 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 862-CoG steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 287 | 164 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 87.8333 | 17 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 917.6 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 38.1732 | 286.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6735.4495 | 747 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 175 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.66664 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.4166 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 695.7166 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14234.6664 | 680 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 58.6666 | 88 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 107.3332 | 280 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1730.5495 | 747 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 38.3166 | 104.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.6059 | 163.32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.0166 | 167 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 337.15 | 61.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 452.2 | 532 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 434.4165 | 401 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 23.85 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 238.9166 | 305 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.06 | 38.02 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 600.6 | 156 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 267.5833 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 90 | 360 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 284.25 | 379 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 744.7999 | 147 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.3 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.5833 | 175 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 120 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.6666 | 200 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 194.773 | 125.66 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 157.4999 | 135 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 146.9998 | 315 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 138.15 | 276.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 357.7 | 147 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 301.6665 | 362 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 66.5833 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 146.6667 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 14.4667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 41.7667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 979.9999 | 168 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 51.3333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1372 | 196 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 27.6 | 69 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 98.1665 | 310 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 201.6 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 140.25 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 289.3333 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 2.8333 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 157.6666 | 86 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 157.25 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1.1667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 60.6666 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 79.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 127.5 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 16056.8333 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 587.3333 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 5526.25 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 99 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 17826.25 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 90 | 36 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1243.75 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 37687.5 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3625 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 3572.4 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 43.05 | 123 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 137.445 | 34.65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Summer | 121.9 | 23 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 20 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 105.7183 | 23.15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 51.45 | 63 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 5286.4349 | 159.39 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 68.6615 | 25.91 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 700 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 16.6667 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 148.2 | 57 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2452.5667 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1.0858 | 13.03 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3.9653 | 14.87 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9.1667 | 12.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 10.8333 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 234 | 180 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 50555.2 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 878 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 23.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4026 | 220 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 18.7833 | 49 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 523.5831 | 305 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 4465.8 | 12 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 67.65 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 268.3333 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 34.4 | 86 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 128.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 35.2987 | 8.68 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.6667 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1320 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1351.5 | 530 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.8333 | 175 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2172.3331 | 380 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 326.2163 | 529 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.25 | 105 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 251.8075 | 143.89 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 387.4659 | 153.96 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10011.8329 | 635 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1441.6665 | 250 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.65 | 529 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 200 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 163.75 | 75 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1906.3406 | 306.65 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3318.3998 | 732 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 550.3372 | 210.32 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2286.792 | 282.32 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304.5 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15314.1832 | 307 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11307.9991 | 1320 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 37.4 | 44 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.943 | 37.58 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.4167 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2605.2164 | 361 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6194.9996 | 531 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136.6667 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127145 | 431 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.8333 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167.2311 | 120.89 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4059.3394 | 775.67 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.25 | 145 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 66.5 | 13.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 87.5 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 22.75 | 35 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 102.6666 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 276 | 30 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 22.1666 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 73.5 | 14.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 562.2667 | 8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Winter | 11740 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 7863.7497 | 405 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 175 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3.65 | 73 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 296.25 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 0 | 0 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 76 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 15053.85 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 12177.1 | 34 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 4.8 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 142.8 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 391.5 | 27 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 10.95 | 73 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 96.9 | 102 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 3.6 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 17 | 170 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 192 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 186.9066 | 65.2 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 465.5 | 190 | 2 | 2 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11.2333 | 2 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.6666 | 140 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.1666 | 70 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.9166 | 95 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 578.1332 | 271 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.6998 | 363 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.46 | 34.82 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6666 | 40 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92.5 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.1166 | 43 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 368.9 | 119 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27 | 135 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.5 | 75 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70 | 200 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1240.6332 | 409 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.5 | 10 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 264 | 96 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 306.5333 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 639.8333 | 110 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 263.7833 | 119 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 612.9632 | 317.05 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.8332 | 125 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29 | 145 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66 | 165 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.6666 | 40 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21 | 90 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 961.3332 | 280 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.8664 | 409 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1015.6832 | 409 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3850.6666 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 157.5 | 126 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362.5 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.2166 | 71 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.4166 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.5 | 91 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.2733 | 65.2 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.5 | 115 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 943.4331 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.9333 | 91 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660.6458 | 83.45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22098.385 | 317.05 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.8 | 22 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 393.25 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288.3999 | 168 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4618.6667 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 77.6967 | 32.6 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2188.0667 | 23 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.6666 | 145 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63 | 105 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6828.0896 | 260.78 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 396.6331 | 326 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.5 | 42 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 379.9999 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.6666 | 350 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.1666 | 125 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.4166 | 125 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.9999 | 165 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1057.1 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2258.0831 | 395 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2262.5664 | 659 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.9343 | 183.19 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 318.5 | 91 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.1667 | 23 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.4167 | 35 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.9999 | 165 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.5833 | 65 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.6666 | 80 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.8333 | 65 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.6666 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1962.6666 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.9166 | 175 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20719.2175 | 317.05 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149.0666 | 104 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.4999 | 165 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 106.25 | 85 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 746.6666 | 160 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1051.8 | 12 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 50.9333 | 8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 78.6166 | 53 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 106.7833 | 43 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 180 | 30 | 1 | 2 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5387.1166 | 263 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8803.96 | 141.24 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 861.6666 | 100 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267.5833 | 95 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 632.7 | 342 | 1 | 1 | 0390-Burner wind boxes and dampers | SF-Startup Failure | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 241 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 276.5 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.1666 | 70 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 221.9999 | 90 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63.25 | 253 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.6667 | 20 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.3333 | 100 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2258.6666 | 40 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 298.4999 | 90 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 910.5832 | 245 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 320.9636 | 310.61 | 1 | 1 | 0400-Burner wind box fires | D2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53110.9162 | 673 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1663.85 | 107 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.6666 | 110 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1383.3333 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1161.6666 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51808.1664 | 770 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 468.3333 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 304 | 120 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 603.3333 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48052.2 | 673 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 735.3 | 38 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 97.9167 | 23.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21024 | 876 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 18.3333 | 44 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1887 | 51 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3766.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 497.8 | 76 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 545.4166 | 85 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 14480.6667 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9765 | 620 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 498.575 | 24.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 531.25 | 125 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 541.9331 | 739 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 118.3999 | 111 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 756.8333 | 38 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 22.96 | 24.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 12.6332 | 379 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 120 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32774.6963 | 490.15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 540 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 21.945 | 23.1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 161.2667 | 23.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 180 | 135 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 473.1999 | 156 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.7 | 86 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 549.1 | 38 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1483.5 | 43 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 49.0665 | 368 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 395.55 | 293 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1378.8831 | 371 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 25.75 | 103 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 186.8333 | 59 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 28.3333 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 108 | 48 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 41.5878 | 108.49 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 42 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 69 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 53.34 | 38.1 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 5.6667 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 104.775 | 38.1 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 5948.3 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 15.0167 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 28.5 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7789.5 | 9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 57.2425 | 32.71 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 30.9167 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2844.1 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 432 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 883.8 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 19.8333 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 657.4167 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 231.3 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 4007.5 | 42 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 16187.7999 | 87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 400.2 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 14.7 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 17423.7 | 63 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 111 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 124.5 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 547.2 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 719.1333 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 51 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 30 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 122.2667 | 8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 858.2 | 42 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 766.8 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 32.02 | 32.02 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 11.6667 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 18.1446 | 32.02 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 88.5 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 431.1 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 32.6667 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 11291.5833 | 35 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 30.1399 | 164.4 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 552 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 17.1 | 18 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 66.0833 | 13 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 860-Co-generator Block
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 2213.75 | 23 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 862-CoG steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 4.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 90 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 733.913 | 60.99 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.259 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.6 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.9667 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3834.811 | 48.82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 103.8333 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.95 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1927.4266 | 135.1 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.06 | 6.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168.0481 | 52.79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1324.7333 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2830.9166 | 161 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 954.85 | 169 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.3333 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.5 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 143.75 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1244.35 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 103.9166 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7.5 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60.5733 | 51.92 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242 | 30.25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250.7833 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.6833 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 47.8333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 141.1666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 648.9 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220 | 40 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 8.75 | 35 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.554 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134 | 33.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 201.96 | 22.44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 219.6833 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1935.8833 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4784.242 | 75.82 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 190.6333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 817.2667 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 88.9333 | 58 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.15 | 6.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.9333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 241.6166 | 133 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.1667 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 400.96 | 50.12 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1136.8499 | 117 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13781.6 | 42.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22082 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.25 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2284.3 | 431 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17 | 8.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.8333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1867.2 | 38.9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.163 | 6.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.8666 | 37 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.0833 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2017.1665 | 190 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.6833 | 91 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.9666 | 101 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1559.1166 | 139 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.695 | 6.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.99 | 9.33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.4 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.25 | 105 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 340.101 | 73.14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 494.65 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.55 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 409.8666 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 534.4 | 167 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 549.0833 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 578.0833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1180 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 28.8 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 567 | 180 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.635 | 6.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.6 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.6337 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.9667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 353.6 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 401.38 | 28.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.4533 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.3333 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.4 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 327.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 530.6666 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 23.4333 | 38 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 120 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 29.5 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 65.45 | 119 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 543.0833 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 82.4166 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 9.1666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 11.8999 | 102 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8.7 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 9.2166 | 79 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 333.3333 | 100 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 50 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 32 | 32 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 350 | 75 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2440 | 32 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 832 | 32 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 76.3 | 42 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 252.45 | 27 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2999.4667 | 32 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 880.5333 | 32 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 60.8 | 32 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 107.7666 | 53 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 814 | 37 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2784.25 | 37 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2015.1 | 27 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 94.5 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1792 | 32 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.3 | 41 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7.4 | 37 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3397.35 | 29 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 252.75 | 45 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 500 | 50 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1327.301 | 64.38 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1090.4 | 54.52 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 50 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7169.3066 | 135.1 | 1 | 1 | 0430-Cyclone furnace | U2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.6667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.9 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.4167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1666 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4667 | 41 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 35 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.75 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3333 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.4 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.4167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.8 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.5 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.33333 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.0833 | 25 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2094.035 | 30.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 92.2833 | 49 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.1667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.05 | 41 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6667 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 20 | 2 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 25 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 25 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.8333 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.1667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99 | 19.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 31.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.45 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.7333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.75 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.7833 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.3 | 6 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.4 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.0666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.7333 | 41 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.9333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.05 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30553.2539 | 157.14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.6667 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.25 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.53333 | 16 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.75 | 15 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.8 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3333 | 20 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8666 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.9167 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6667 | 20 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 41 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 343.6166 | 53 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.0667 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.8333 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.1 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.532 | 6.18 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.1667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.0333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.65 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.2667 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.6666 | 25 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.9167 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.6667 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.6667 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.75 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18.6333 | 43 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2877.63 | 135.1 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.66666 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.99999 | 15 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.0667 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 20 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.1666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.25 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.2 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.8 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.05 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.2833 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.0333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1 | 41 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.0833 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.2 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.3 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.25 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.3333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.1833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.66666 | 20 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.99999 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.25 | 25 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.2 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.75 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.15 | 43 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 42 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.0333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.5 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.4167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.5 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.6666 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.16667 | 5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.5 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.8333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6667 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.6833 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.9 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.1 | 42 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 42 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.3666 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4167 | 41 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.15 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.3666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.25 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.9387 | 12.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.6667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0.83332 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5833 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5.7333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 15 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 20 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.3 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.6 | 16 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.75 | 15 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3333 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5 | 35 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.3 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.8333 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116 | 23.2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.33333 | 10 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 26 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8333 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3333 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.45 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.7666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.3833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.35 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1666 | 25 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 17 | 51 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 906 | 20 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 68.4666 | 79 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11840 | 800 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21102.6658 | 1330 | 1 | 1 | 0440-Fuel oil pumps (general) | SF-Startup Failure | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2080.4999 | 342 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 498.3 | 830.5 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | SF-Startup Failure | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 55.4666 | 128 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 94.9666 | 37 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 17.4166 | 95 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 30.0333 | 106 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2819.7 | 234 | 1 | 1 | 0460-Fuel oil atomizers | SF-Startup Failure | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 29.3333 | 80 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.9997 | 510 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1760.9163 | 565 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 377.6133 | 25.4 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 444.5 | 30 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 3141.98 | 25.4 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 725.17 | 25.4 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 3710 | 30 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 855 | 30 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 654.5 | 154 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 14145 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2714 | 118 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2873.3 | 48.7 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 125274.1333 | 136 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 742.2158 | 115.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 182.9333 | 56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 817.3999 | 183 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1031.9999 | 288 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 202.2421 | 205.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 39.2 | 49 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 443.5185 | 195.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 738.2534 | 95.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5795.0831 | 353 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3080.5333 | 32 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 546 | 390 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98 | 98 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189 | 140 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21546 | 133 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1184.9998 | 450 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4015.9999 | 240 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3240.75 | 435 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 34795.6497 | 495.9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 111.6 | 31 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 80.4666 | 68 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2937.2 | 56 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5137.79 | 115.89 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2885.1 | 48.9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7156.6664 | 475 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 221.6666 | 100 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 579.4999 | 183 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 135 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 111.8333 | 61 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1999.2432 | 315.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 65772.2 | 533 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2317.7 | 86 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 117616.2665 | 536 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10411.583 | 515 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14908.9333 | 124 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2669.1 | 434 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 61126.2165 | 533 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 102.3 | 9.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 214.7 | 11.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 135.1 | 19.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45.9 | 15.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 105.6867 | 8.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 259.9 | 11.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 150 | 150 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 250 | 250 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 115.8999 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 32.9666 | 46 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 123.5 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 661.2 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 85.5 | 114 | 1 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 108.3 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 119.7 | 114 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 587.52 | 91.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 504.56 | 296.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 429.45 | 286.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 553.4998 | 332.1 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23986.6666 | 175 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 768.5173 | 16.48 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13043.3328 | 728 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2467.88 | 16.48 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.5 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2859.5 | 190 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 273 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18345.6 | 196 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6154.9998 | 300 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 74.1667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18706.8 | 17.85 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 419329.5997 | 411 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.5 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42326.0331 | 661 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37426.1331 | 832 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7243.0332 | 197 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29064.333 | 446 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 157496.1662 | 677.5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 183875.1 | 691 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2989.8 | 198 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 26393.75 | 123 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4062.4999 | 150 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 182.4 | 114 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 44241.0749 | 310.5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 35.6965 | 14.57 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 450.45 | 273 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1218.9998 | 276 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 6454.2999 | 114 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1424.1498 | 273 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 29473.5832 | 185 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 3893.3333 | 80 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 30201.25 | 185 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 29439.6666 | 185 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2141.3333 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 53627.9166 | 335 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4199.75 | 535 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18920.9064 | 330.4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58602.5 | 550 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 61.3333 | 20 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855.4665 | 401 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 950.4 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4212.5 | 125 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5476.1667 | 22 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 20201.1663 | 610 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16042.6664 | 752 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1894.5466 | 60.4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2016.7 | 120.4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.5 | 51 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 107369.6 | 29 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25215.6331 | 742 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27943.515 | 404.1 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 338.3333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 72 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.5 | 31 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1312.9331 | 344 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1042.0666 | 58 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1990 | 199 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 586.25 | 35 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36264.6658 | 1330 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 26869.3498 | 369 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 238.95 | 8.85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.5333 | 71 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36562.1664 | 770 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3301.4933 | 16.48 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.3333 | 106 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 254.1999 | 123 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1771.415 | 13.85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26970 | 600 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3333 | 20 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14985 | 405 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7950.2 | 626 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10880.9166 | 115 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2355.9199 | 180.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 735.5332 | 236 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1265.3332 | 146 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27553.9998 | 345 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 319.3 | 206 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 986 | 232 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 118.8333 | 115 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 800-Miscellaneous
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5352.6665 | 518 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1944.8 | 33 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2525.25 | 45 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 2274.75 | 9 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 20.3866 | 55.6 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1102.0665 | 244 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 314.9999 | 378 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 18279.6665 | 244 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 27.45 | 183 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 349.0666 | 176 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 115.8 | 193 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 77.4683 | 87.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 101.9999 | 153 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 2048.6666 | 140 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 21178.8 | 199.8 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 345 | 150 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 7471.3332 | 140 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1243.8333 | 85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 533.4166 | 185 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 112.6666 | 169 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 8.42 | 168.4 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4536.1666 | 85 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 754 | 104 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 27.9998 | 240 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 4373.6 | 24 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 860-Co-generator Block
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22056.75 | 490.15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 1.75 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.92 | 6.87 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12951.6 | 258 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.96 | 3.81 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 3.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 194.92 | 8.86 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 1549.611 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.35 | 6.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30900.3331 | 595 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.0667 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 4 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64 | 12.8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 3.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 109.25 | 115 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 23.28 | 23.28 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.92 | 4.62 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 6 | 1 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 3.75 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33 | 5.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 100 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63 | 10.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.08 | 4.44 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 4 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 2 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.96 | 6.44 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 167.02 | 23.86 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2105.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7614.5831 | 425 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 3750 | 30 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.92 | 6.12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.96 | 7.31 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13 | 6.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34175 | 500 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 467.5 | 102 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 795.6 | 102 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 787.8 | 18 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 3418.8 | 111 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 694.7865 | 194.8 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1251.2 | 51 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 15747.1999 | 111 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 70.2999 | 114 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 146.3 | 114 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 228.7333 | 73 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 2439.4166 | 73 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1622.8498 | 279 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 256.9333 | 82 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1403.5 | 42 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 602.8974 | 103.65 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30184.9998 | 300 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392.3333 | 220 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 720 | 48 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 101.6667 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 617.5 | 10 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3100.7998 | 342 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2423.3733 | 68.2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 397.75 | 185 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 1055.5999 | 168 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 11187.3999 | 183 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 3477.2165 | 193 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9605.7665 | 275.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 4908.4915 | 275.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 4585.5333 | 169 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 12040.9332 | 271.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 348.5532 | 271.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 56765.7333 | 172 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 1555.2 | 192 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 367.3332 | 275.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 52254.7999 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 1088.225 | 275.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 1201.7 | 197 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 992.7666 | 158 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 3944.5 | 161 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 153.4 | 236 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 215.0665 | 322.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 6230.7 | 322 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 170.1333 | 116 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 252 | 126 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1027.5 | 75 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1531.1 | 251 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 9202.5 | 150 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 3941.8166 | 161 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D3-Forced - Postponed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 844.1365 | 322.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 207.0016 | 161.3 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 4843.7997 | 486 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 99.4682 | 161.3 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 2834.59 | 160.6 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D2-Forced - Delayed | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 2984.6666 | 110 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 348.2997 | 486 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 24240.3333 | 110 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810 | 324 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 11673.7498 | 495 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 1428.8 | 150.4 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6529.5999 | 168 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 3714.3466 | 151.4 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 20899.7332 | 149 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 2261 | 238 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1649.2582 | 171.5 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 654.3666 | 134 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2397.5 | 105 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1186.5833 | 145 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1560 | 130 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32823.52 | 81.3 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 30494.4999 | 213 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 800-Miscellaneous
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 612.4999 | 147 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 738.1612 | 165.26 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 5881.3332 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 22230.9669 | 225.39 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 1185 | 237 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 5573.3332 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 16242.5333 | 172 | 1 | 1 | 0550-Reheat steam relief/safety valves | U3-Forced - Postponed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 1704.6946 | 164.44 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 1941.8666 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 218.05 | 147 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 7.8999 | 237 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 698.87 | 164.44 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 5356.2666 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 1757.2646 | 165.26 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 1734.0498 | 237 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 16012.75 | 169 | 1 | 1 | 0550-Reheat steam relief/safety valves | U3-Forced - Postponed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1092.2665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 8531.2 | 248 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 19687.5 | 210 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 3016 | 232 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 18196.6833 | 193 | 1 | 1 | 0550-Reheat steam relief/safety valves | U3-Forced - Postponed | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 638.75 | 25 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2713.6 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4885.6 | 248 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 24440 | 160 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 54386.2 | 419 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 551.7998 | 534 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 423.7997 | 489 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 546.7664 | 698 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1226.5549 | 95.7 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 199.9997 | 480 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 391.9997 | 480 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 22769.7082 | 193.1 | 2 | 2 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 76.2499 | 183 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1016.2165 | 253 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2374.1332 | 307 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 1013.3333 | 160 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 22471.15 | 181 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 736.3999 | 168 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1775.4832 | 307 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 4534.5665 | 298 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 12458.635 | 167.23 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3474 | 193 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 20805.4 | 196 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 119117.9667 | 38 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 460.25 | 105 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1348.2 | 160.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6080 | 304 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 729.3 | 187 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1056.6249 | 160.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 22934.7915 | 194.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5076 | 282 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18916.3328 | 770 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 5319.3498 | 573 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 306.1332 | 328 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 415.4664 | 328 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 48.0333 | 22 | 2 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1111.5999 | 168 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1105.2 | 307 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1472.7999 | 168 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 660.05 | 307 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 938.9999 | 180 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2363.75 | 152.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 179.3833 | 229 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2127.8332 | 170 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 1588.6499 | 153 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 787.9665 | 307 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3241.3332 | 176 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 632.875 | 152.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 639.5832 | 307 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 1954.3332 | 164 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1946.0833 | 193 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 2312.8 | 196 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 622.5 | 150 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 714.6832 | 137 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 11460 | 240 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 3813.3332 | 286 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1976.3333 | 196 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1923.3249 | 160.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 436.0249 | 160.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 173.7999 | 237 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Winter | 996.8 | 96 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 265.9999 | 120 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1811.7666 | 113 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1143.9999 | 96 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2360 | 200 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 187.7666 | 86 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 131.5 | 263 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 569.775 | 160.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 2050 | 410 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2043.9 | 378.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2325 | 150 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.3333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 3.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.8333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 282.6333 | 61 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 10.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 257 | 257 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.8 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 998.3833 | 37 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 37.9167 | 35 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 367491.7997 | 843 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 5.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39 | 7.8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.96 | 6.37 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 855 | 57 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.98 | 6.14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3166 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 23554.7831 | 419 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 551.4165 | 509 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 338.2666 | 236 | 1 | 1 | 0570-Other reheat steam problems | U2-Forced - Delayed | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 217.8666 | 152 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 144.6525 | 64.29 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 7245.0832 | 227 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 150.4125 | 66.85 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 184.5 | 246 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1602.4666 | 172 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1634 | 172 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Summer | 196.08 | 261.44 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 163.1999 | 153 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 45 | 225 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 966.7666 | 194 | 1 | 1 | 0570-Other reheat steam problems | U2-Forced - Delayed | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7858.3165 | 193 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 2355.9665 | 322 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3990.2333 | 98 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 109.9125 | 48.85 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 32 | 160 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 69.8333 | 10 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 170 | 10 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16312.0832 | 275 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14434.8 | 552 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 30015 | 450 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102996.2498 | 525 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53844.0831 | 389 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43732.2664 | 448 | 1 | 1 | 0580-Desuperheater/attemperator piping | U2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5606.34 | 264.45 | 1 | 1 | 0580-Desuperheater/attemperator piping | U2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 344.75 | 105 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2534.7 | 357 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 140.03 | 127.3 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3813 | 310 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 979.05 | 107 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 326 | 326 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 706.35 | 277 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 157.3 | 121 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1184.1665 | 350 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4891.75 | 51 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5188.1332 | 233 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 654.3666 | 293 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 910 | 91 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1024.25 | 241 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1276 | 290 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132.5 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 852 | 142 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2857.0664 | 352 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1084.9998 | 300 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21904.5331 | 613 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54.2667 | 22 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 541.1666 | 170 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1289.1666 | 91 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5375.9998 | 315 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.01 | 8.67 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1893.6666 | 115 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41286 | 60 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 399.5 | 141 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1730.55 | 83 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 454.9165 | 265 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 802.2333 | 41 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5589.5415 | 205.75 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 83.36 | 41.68 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 91.12 | 45.56 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 110 | 55 | 1 | 2 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 146.32 | 36.58 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 50.4166 | 55 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 4788.9499 | 213 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 800-Miscellaneous
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.083333 | 0.1 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 12949.0162 | 642.1 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4412.6667 | 10 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 44.2 | 221 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1890 | 315 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.4 | 6.87 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3981.2498 | 525 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 637.2166 | 221 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.34 | 3.34 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15978.0498 | 627 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U2-Forced - Delayed | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8138.5332 | 179 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20016.8741 | 97.13 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2262 | 377 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4879.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19024 | 820 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 32524.9995 | 750 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2025.833 | 850 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19622.4 | 336 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30370.9996 | 660 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 830 | 200 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 326.8332 | 370 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22434.6664 | 752 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13791.6664 | 331 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4446.6666 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38491.4833 | 91 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4508.9998 | 324 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2846.0997 | 477 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99577.3328 | 752 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4745.25 | 855 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 521536.3996 | 1239 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1636.2661 | 832 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 361.6665 | 434 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 107443.9165 | 533 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6903.6 | 264 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | SF-Startup Failure | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28392.5 | 692.5 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52762.4996 | 1350 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23484.0465 | 316.71 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U2-Forced - Delayed | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36159.9996 | 600 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1129.5662 | 658 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4174.5 | 330 | 1 | 1 | 0660-Other startup bypass system problems | SF-Startup Failure | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3274.9995 | 750 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 39357.05 | 311 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13291.9999 | 240 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 22008 | 240 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5465.7832 | 191 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 258.075 | 11.1 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 259.2 | 64 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1722.6666 | 64 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 14.4 | 36 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1.0666 | 64 | 1 | 2 | 0670-Feedwater piping downstream of feedwater regulating valve | SF-Startup Failure | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 9303.4666 | 64 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U2-Forced - Delayed | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 626.4 | 81 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 860-Co-generator Block
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1640.4166 | 25 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14527 | 73 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 674.1 | 107 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2908.8332 | 155 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 749.9997 | 450 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1437.9163 | 493 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8195 | 745 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8565.5 | 370 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.277 | 33.83 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 406.8545 | 35.43 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4112 | 257 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8279.5832 | 155 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1322.3998 | 342 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 551.05 | 107 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 415.2499 | 165 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2857.2499 | 165 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 487.6667 | 35 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19862.8332 | 370 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.4268 | 37.21 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.4999 | 105 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22535.3328 | 770 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 400.95 | 243 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1254 | 209 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 754.05 | 457 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 68.42 | 74.64 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 32751.6664 | 457 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 779.5666 | 257 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 2201.625 | 142.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 15.6 | 36 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 120.8 | 151 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 7661.6832 | 253 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 264.4499 | 193.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 191.6667 | 50 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 169.4667 | 41 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 4379.3999 | 162 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 230.9583 | 120.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 770.6666 | 170 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Winter | 119.0666 | 188 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 861-CoG GT units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | NPCC | Off-Peak | 745.2 | 46 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 861-CoG GT units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 39.2666 | 62 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 862-CoG steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.4 | 12 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 88.3333 | 20 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3.3333 | 40 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.25 | 25 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.25 | 45 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 369 | 36 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2483.3331 | 745 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.5 | 35 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6766.4996 | 585 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 687.4995 | 750 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 71.5 | 55 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 38.5 | 22 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5337.4995 | 750 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24517.4158 | 1231 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5737.5 | 750 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6562.5 | 750 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 619.4 | 16.3 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 800-Miscellaneous
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2023.8866 | 279.8 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 926.44 | 174.8 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 292.5083 | 159.55 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 313.3666 | 158 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 146.25 | 75 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 587.2426 | 275.27 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 19.0833 | 229 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 2254.2665 | 232 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 233.2883 | 20.14 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2304 | 96 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2682.4068 | 97.13 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 24807.1998 | 528 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 4198.9998 | 255 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 949.8333 | 82 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 118.5285 | 253.99 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 402.1507 | 253.99 | 1 | 1 | 0720-Blowdown system controls / instrumentation | SF-Startup Failure | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 2249 | 173 | 2 | 2 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 851-CC GT units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2197 | 169 | 1 | 1 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 852-CC steam units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 15384.5999 | 162 | 1 | 1 | 0720-Blowdown system controls / instrumentation | D1-Forced - Immediate | 852-CC steam units
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13995.6666 | 347 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 145.6033 | 45.98 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 18465.9999 | 168 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 851-CC GT units
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 9920.1333 | 94 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14367.75 | 45 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 34004.25 | 595 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 36703.4 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6960 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2350.8331 | 350 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18074.233 | 497 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4989.628 | 171.76 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42312.7332 | 268 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 40 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1370.6666 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 618.6915 | 571.1 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9805 | 530 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1600 | 32 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.6666 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68145.0663 | 544 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 722.7499 | 177 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 165.3333 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 361.9999 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10154.6665 | 476 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23025.5832 | 415 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39119.6163 | 613 | 1 | 1 | 0740-Boiler recirculation pumps | U3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3642.3666 | 113 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 11410.4 | 68 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 393.8997 | 454.5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 16398 | 72 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 851-CC GT units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 4125 | 44 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 28538.5998 | 372 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4312.4999 | 450 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5375.4166 | 97 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 175.75 | 95 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 25670 | 68 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 318 | 530 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81967.3328 | 740 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12137.3333 | 80 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101731.7 | 57 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1025.25 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7830.55 | 91 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2766.3328 | 860 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3218.5997 | 462 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1628 | 80 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7496 | 80 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9523.6999 | 393 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 928560 | 106 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15464.0998 | 342 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10391.6665 | 500 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14763 | 380 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U2-Forced - Delayed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 466834.6165 | 491 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U2-Forced - Delayed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 4320.3333 | 26 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 800-Miscellaneous
0750 | Boiler recirculation piping including downcomers | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 459.03 | 235.4 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 851-CC GT units
0750 | Boiler recirculation piping including downcomers | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 41.1667 | 5 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 852-CC steam units
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 370.2397 | 427.2 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 860-Co-generator Block
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 3678.3131 | 417.2 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 860-Co-generator Block
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 137.4998 | 330 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5308.3996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 147.6 | 246 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 850-Combined Cycle Block
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 15.1666 | 130 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98.6 | 116 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 178.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 146.0333 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 389.25 | 173 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 6529.35 | 275.5 | 1 | 1 | 0770-Other boiler recirculation problems | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28075.7 | 446 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51574.2 | 516 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4583.1329 | 644 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17172.5164 | 427 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10928.4998 | 330 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67473 | 245 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4036.6665 | 175 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 882.495 | 24.3 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 650-Fluidized Bed
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2185.2 | 182.1 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1476.7999 | 213 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 248007.2 | 268 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 2126.2165 | 193 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 2295 | 150 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1728.9 | 113 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 1599.7 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 14283.7499 | 225 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 446.2499 | 225 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 860-Co-generator Block
0780 | Headers between tube bundles | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 292.5 | 10 | 1 | 1 | 0780-Headers between tube bundles | D2-Forced - Delayed | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42679.9999 | 330 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1052.555 | 176.9 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 850-Combined Cycle Block
0782 | Headers and caps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 10620.5181 | 311.3 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 850-Combined Cycle Block
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 861 | CoG GT units | WECC | Summer | 26865.9999 | 168 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U3-Forced - Postponed | 861-CoG GT units
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 36122.2833 | 223 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U3-Forced - Postponed | 862-CoG steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 6042.5 | 150 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 509.3999 | 108 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 17463.5 | 659 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 30.6525 | 30.15 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3755.4994 | 870 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29668.5 | 342 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 704.1666 | 32.5 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 193.8 | 32.3 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 253.5 | 13 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1933.8998 | 249 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8236.8166 | 273.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1213.6998 | 318 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 81725.3329 | 608 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 7.3333 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 5104.14 | 87.7 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 2440.1666 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 4740.185 | 87.7 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 11029.0832 | 245 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 5.5 | 55 | 1 | 2 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1171.1 | 167.3 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 2.75 | 55 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 418.25 | 167.3 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4701.6 | 144 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 25394.1999 | 156 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 12133.3332 | 250 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3344.0499 | 141 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 6212.2666 | 128 | 1 | 1 | 0799-Other miscellaneous piping system problems | D3-Forced - Postponed | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 274.4 | 49 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4427.8399 | 164.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 11558.4 | 256 | 1 | 1 | 0799-Other miscellaneous piping system problems | U3-Forced - Postponed | 852-CC steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 30.1 | 86 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 861-CoG GT units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 15 | 30 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 862-CoG steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.6 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 505.559 | 466.67 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5769.75 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6879.9 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2637.25 | 385 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.9 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 314.4 | 262 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 768.6 | 427 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32154.5331 | 691 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 722.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.5 | 86 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 148.2666 | 64 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1041.7549 | 437.1 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4799.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 608 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 22005.625 | 642.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1527.6 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1940 | 48 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 19.8 | 27 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 472.4997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1176.9998 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1694.1666 | 107 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1784.1 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.8333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 467.4998 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14543.0832 | 535 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 545.7499 | 111 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 1652.4 | 136 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 8683.4166 | 79 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 800-Miscellaneous
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 4894.05 | 79 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 800-Miscellaneous
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 7541.8666 | 79 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 800-Miscellaneous
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1618.2666 | 106 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 705.1999 | 258 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 27.45 | 183 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 119.5999 | 156 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 119.5999 | 156 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 6785.25 | 83 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 201.4833 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 52.3333 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 172.7 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Off-Peak | 810.3332 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 47.9166 | 115 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2536.9283 | 50.57 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 28.4683 | 58.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 801.9265 | 194.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 14772.0829 | 605 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 432.833 | 530 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 146.3 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 165.3 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 474.0133 | 194.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 43.3333 | 40 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 5196 | 240 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 619.3599 | 379.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2923.8332 | 331 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11427 | 22.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 26744.7749 | 171.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 8 | 30 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 979.5999 | 379.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9207.7333 | 236.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 46.075 | 28.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 72.5 | 30 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1821.38 | 194.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 162.1499 | 207 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 26077.9999 | 312 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 788.7399 | 418.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 65.5499 | 207 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7788.7333 | 236.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 250.583 | 485 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 438 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1167.1665 | 298 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 312.9 | 149 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 700.6249 | 142.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 3339.7 | 182 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 564.8499 | 237 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 3706.5749 | 328.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 85.5499 | 177 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 5984.5333 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 33552 | 192 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 34425.75 | 197 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 88.9666 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 262.9248 | 222.19 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 595.2 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 163.1999 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 123.5 | 247 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 761.2499 | 225 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 87.6 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 695.8665 | 307 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Summer | 480.9 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 504.2465 | 175.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 131.7666 | 67 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 233.0499 | 237 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 37.325 | 149.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 109.5666 | 173 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 255.6 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 4361.8666 | 176 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 8188 | 178 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 4662.9 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 4692.6 | 158 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 529.65 | 160.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 934.5 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1388.4 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 305.4665 | 232 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 827.4799 | 164.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 853.7841 | 149.35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 27148.6249 | 172.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 962.4232 | 322.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 2095.5999 | 372 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3.6667 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 1669.85 | 91 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 315.525 | 150.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 142.9332 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 43862.25 | 251 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 3109.8666 | 119 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 112.7 | 322 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 234.6666 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 418.3 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 179.2 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 20.2216 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 95.9999 | 144 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2217.2462 | 180.02 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 27.825 | 111.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 180.2666 | 169 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 248.4999 | 210 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Winter | 174.9999 | 300 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 54.9666 | 97 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 140.8 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3999 | 372 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 129.2958 | 221.65 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3438.9332 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 247.4665 | 232 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7.2333 | 62 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 31.2516 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 56.3666 | 89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 64 | 128 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 1193.4 | 81 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | WECC | Winter | 35.7795 | 238.53 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 1725.0166 | 83 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | NPCC | Off-Peak | 6.8 | 24 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 143.2 | 179 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 189.7133 | 79.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | WECC | Winter | 7259.4333 | 178 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 3800 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 196.6666 | 236 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 562.4666 | 236 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 269.3333 | 80 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 4690.0833 | 115 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 18.4332 | 158 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 229.8915 | 281.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 281.5265 | 383.9 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 256.6498 | 531 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 169.7332 | 268 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 298.4499 | 381 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 679 | 485 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 4632.56 | 293.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 82.88 | 103.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 11301.6 | 277 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 675 | 300 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2008.0999 | 258 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.1333 | 16 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 134.7666 | 155.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 4562.1333 | 208 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 68.7499 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 140.4 | 234 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 740.6333 | 222.19 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 91.8 | 153 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 333 | 180 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11.8665 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 103.8 | 173 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 715.2132 | 271.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 12.9833 | 41 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3885.4832 | 227 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 1653 | 275.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 157.9998 | 237 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 16.275 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 138.2499 | 237 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1957.2333 | 142 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 194.25 | 105 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 120 | 300 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 9.6075 | 27.45 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 427.445 | 161.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 2895.2 | 132 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 52.7333 | 113 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 37.2165 | 319 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 949.3998 | 282 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 13.775 | 43.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 377.3999 | 306 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 54.3832 | 251 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 105.1333 | 83 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 441.4665 | 301 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 66 | 132 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 59.1999 | 96 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 9.9332 | 149 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 107.7999 | 132 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 4418.7499 | 375 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 699.9999 | 210 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0.46667 | 3.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 8.3666 | 251 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 52.6703 | 225.73 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | SERC | Summer | 107.2 | 134 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 2267.4166 | 169 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 3672.0833 | 175 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 862 | CoG steam units | SERC | Summer | 88 | 110 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 70.65 | 157 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 751.75 | 485 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 6039.92 | 293.2 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 856.833 | 485 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 93.6 | 104 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 359.1 | 378 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1582.4 | 197.8 | 2 | 2 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 68.8499 | 243 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 230.0999 | 234 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 1691.2498 | 225 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 1807.4999 | 225 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3058.2699 | 176.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 677.9999 | 180 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 5137.185 | 172.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 950.9999 | 180 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 783.1666 | 185 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3286.13 | 176.2 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 5274.4 | 152 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 27.8 | 139 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 257.25 | 105 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 801.95 | 43 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1109.4999 | 210 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Summer | 4501.38 | 150.8 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 2570.6666 | 320 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 2108.8 | 263.6 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 395.4999 | 105 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 273.7498 | 225 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 746.7666 | 43 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 233.55 | 173 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 713.8 | 172 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 645 | 172 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 139.347 | 103.22 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 369.075 | 98.42 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 408.443 | 98.42 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1070787.9998 | 552 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 59320.8 | 749 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 299.1772 | 267.92 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 850-Combined Cycle Block
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 1119.1499 | 81 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U2-Forced - Delayed | 860-Co-generator Block
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6974.3025 | 344.41 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10227.8516 | 259.7 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 9118.8666 | 86 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3898.661 | 260.78 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31991.2833 | 43 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31992 | 43 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18480 | 15 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 514.0135 | 112.97 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5130.33 | 264.45 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81924.9994 | 870 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13335.5 | 358 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29015.35 | 39 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 266.17 | 61.9 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27456 | 44 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31724 | 44 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32735.2667 | 44 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 576.9166 | 215 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28949.25 | 435 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 33316.6666 | 50 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6048 | 63 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30240 | 42 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4207.5 | 225 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26783.4 | 36 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28799.3333 | 40 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1507.5667 | 26 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11338.05 | 393 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2079 | 45 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 650-Fluidized Bed
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 15450.2332 | 319 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 202.3 | 289 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7368.8999 | 198 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 798.3666 | 86 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7884.4997 | 390 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5820.5333 | 208 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1500 | 25 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.9725 | 48.45 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 686.4 | 312 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 375 | 125 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2673.3199 | 127.2 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11321.4899 | 142.2 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6474.4533 | 140.8 | 1 | 1 | 0830-Doors | SF-Startup Failure | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 17762.7749 | 166.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 286.65 | 147 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 14574.9166 | 145 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 173.25 | 165 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 4557.0175 | 167.23 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 16299.9999 | 150 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 14574.9166 | 145 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4644.3166 | 101 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8041.2833 | 101 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1259.175 | 51.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | WECC | Summer | 547.4 | 23 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Winter | 806.8333 | 94 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 454.9166 | 53 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 68573.8664 | 448 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1495.8 | 27 | 1 | 1 | 0840-Refractory and insulation | D3-Forced - Postponed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4311.5626 | 260.78 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 286.65 | 39 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 457.9165 | 175 | 1 | 1 | 0840-Refractory and insulation | SF-Startup Failure | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 3000 | 90 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 40280.9666 | 179 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 851-CC GT units
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5874.5829 | 575 | 1 | 1 | 0845-Windbox expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 807.55 | 260.5 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46197 | 261 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8918 | 13 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10624 | 8 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2586.7833 | 13 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2111.25 | 45 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 34881 | 330 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 108630.8331 | 610 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 6801 | 45 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 21.3333 | 20 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 800-Miscellaneous
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 34992.1164 | 421 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 850-Combined Cycle Block
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157890.8999 | 306 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 38678.4998 | 258 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 640.6999 | 258 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 489.8333 | 5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 57.9666 | 37 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2604.9832 | 143 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1040 | 80 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1832.4952 | 242.18 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 229.6667 | 20 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 324.5 | 118 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2210.1 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 297.0166 | 71 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 397.885 | 25.67 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1755.6 | 77 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 2423.9366 | 277.55 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 1467.3333 | 71 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 12.25 | 5 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 21475.8665 | 298 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105504.8165 | 497 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21949.6665 | 322 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.05 | 99 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 387.5 | 31 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1411.1333 | 244 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35970.0345 | 56.57 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.9666 | 62 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 656.3333 | 22 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.1499 | 219 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301 | 172 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344.0667 | 26 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.5 | 10 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5333 | 16 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.9 | 28.6 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.2 | 32 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.2 | 57 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.9333 | 26 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2682.4 | 112 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 313.3333 | 25 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.5 | 22 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.05 | 93 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.7 | 66 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 45 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 498 | 166 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.5 | 21 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.77 | 24.6 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228.0833 | 35 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267.3667 | 26 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 269.5833 | 25 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.4166 | 31 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510 | 34 | 2 | 2 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.01 | 39.77 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.65 | 57 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8048.565 | 53.55 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 263.9 | 20.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 54.9 | 18.3 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 800-Miscellaneous
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 30940.0165 | 383 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 560 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 273 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 684.2166 | 61 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1086.6666 | 200 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1 | 1.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.5 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1029.5666 | 67 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2101 | 382 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9137.7333 | 76 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 635.6973 | 53.57 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 813.9 | 271.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.0667 | 47 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.58333 | 0.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234.8666 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255.9998 | 240 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.8143 | 4.54 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 3.7333 | 4 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.8333 | 25 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1331.9999 | 270 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 379.9133 | 116.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 526.4 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 684.6016 | 166.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1028.9999 | 126 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2530.4 | 316.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4981.725 | 316.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 642.5833 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1206.25 | 25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290.5 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 370.3 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 388.5 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 801.8666 | 62 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1322.4 | 174 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5194.1999 | 198 | 1 | 1 | 0870-Soot blowers - steam | U1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 445.2 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15 | 150 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 652.3916 | 60.5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.5283 | 61.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 5.9 | 6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 6.6 | 6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395.5 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 893.5333 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 65 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.8 | 47 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.5 | 70 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204.176 | 6.72 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1223 | 20 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.1 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.6 | 166.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 681 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1492.3333 | 20 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2985.47 | 82.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 606.2 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1678.35 | 167 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 0.95333 | 1.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1581.5 | 316.3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6125 | 500 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.6 | 42 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 773.5 | 71.4 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 791.5331 | 383 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 0.12 | 0.6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.2 | 4.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4 | 4 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.5 | 4.5 | 1 | 2 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4.1 | 4.1 | 1 | 2 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3.8 | 3.8 | 1 | 2 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Oil | OL | 800 | Miscellaneous | MRO | Winter | 760.55 | 14.35 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 800-Miscellaneous
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 754 | 116 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.3 | 37 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2932.8 | 141 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 409.275 | 25.5 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 558 | 27 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1355.7333 | 31 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1480.2333 | 48.4 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.5 | 19 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.1833 | 43 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.1333 | 53 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.55 | 63 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 432.3666 | 152.6 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2431.9999 | 120 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4724.5833 | 25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.1833 | 7 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94 | 40 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88 | 110 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 175 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1908 | 53 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376 | 80 | 1 | 1 | 0876-Soot blower controls | U1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 186.0833 | 77 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1272 | 212 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1847.3333 | 40 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.5 | 39 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 99.75 | 95 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.95 | 93 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2767.5 | 246 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2418 | 93 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675 | 150 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13410 | 120 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.2 | 63 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.5 | 15 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 92.6333 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760 | 380 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 122.445 | 27.21 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 120.1333 | 17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 263.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 756.6667 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4486.5332 | 418 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2470 | 380 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 747.5 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 545 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 9.45 | 9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1238.5832 | 167 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2770.752 | 144.31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 59.5 | 17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 64.5 | 18 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2418 | 155 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5323.9999 | 330 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 75.54 | 12.59 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40696.9166 | 335 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 852.5 | 155 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5940 | 330 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4211.2 | 224 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 56.1 | 22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38566.3328 | 740 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | SF-Startup Failure | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1213.3333 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 300.6666 | 88 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 352 | 88 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 148.1533 | 31.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 264 | 33 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 15508 | 80 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 5379 | 326 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 195261.9162 | 769 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 4480 | 448 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3312 | 480 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2717.8666 | 224 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3229.0332 | 146 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 407.25 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1392.3333 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95093.4995 | 690 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 11272.5 | 675 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6804.834 | 206.52 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19266.6664 | 340 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20144.7998 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12565.1498 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 610.008 | 290.48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 386.6666 | 40 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5305.5 | 393 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8744.25 | 393 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 48.5 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 216.9667 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139.5 | 27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6557.1998 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24017 | 658 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4370.4 | 144 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 848.5 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2520.8333 | 250 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3773.66 | 171.53 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1250.3333 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 492.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14094.6 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.6 | 36 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.75 | 49 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1874.1666 | 130 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.5113 | 14.62 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 949.13 | 73.01 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1094.5 | 110 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1149.5 | 110 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9471.46 | 136.28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 263.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17192.79 | 206.52 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5059.9998 | 600 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276 | 230 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5739.0749 | 310.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 2 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 205.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 242.5 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 44.1667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8520.1664 | 469 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469.9998 | 600 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50265.3729 | 700.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 35.42 | 7.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 724.8833 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 12.5 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22599.9996 | 600 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680730.5829 | 635 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 647.25 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30910.0997 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 379.1666 | 130 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1350 | 180 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105.4 | 124 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 326.97 | 140.13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3489.1665 | 395 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10805.1333 | 244 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1409.6832 | 301 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1561.8 | 274 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 580.679 | 143.97 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2603.68 | 162.73 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3564.659 | 164.27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2041.0249 | 160.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 127.65 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 99.9 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 35 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8264.1 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 46 | 9.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 260 | 32.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 10140 | 32.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 211.6283 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 234 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 54.9 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | BM | 800 | Miscellaneous | WECC | Winter | 147.915 | 17.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 100.1 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 656.1 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1171.35 | 27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 31.5 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 37.2 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 87.9 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91.5 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 214.5117 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 735.3283 | 28.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1064.2 | 31.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 58.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 71.5 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 156.1 | 22.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 162 | 27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 24.9 | 8.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 77.2 | 19.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 131.9383 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 171.6 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 85.2 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 350.1117 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 582.795 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 994.0283 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 170.4 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 281.7 | 31.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 946.8 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 81.5 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 156.5 | 31.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 553.445 | 21.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 73.2 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 171.6 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1261.9617 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 90.4 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 403.2667 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 60.9 | 20.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 245.7 | 27.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 286 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.4667 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 332.1 | 12.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 425.3783 | 13.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1141 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 79.1 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 141.5 | 28.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 328.7 | 17.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 394.5 | 26.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 130.4 | 16.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 114.4 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 41.2 | 10.3 | 1 | 2 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 139.8 | 23.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 558.3783 | 13.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 297.6 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2622.5333 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 75 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 888.5333 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 75 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 995.25 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 575 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 387.5 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 758.9333 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 660.3 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 124.8 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 214 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1201.25 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1904 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3572 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 399.4666 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 555.8333 | 29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1274.7167 | 17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1450.3667 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 573.3333 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 48.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 49.1667 | 10 | 1 | 2 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 83.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19615.0665 | 524 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 960 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1466.9999 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2947.7499 | 195 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12613.3333 | 220 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 209.1667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 35.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 47.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27742.8664 | 442 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1417.5 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 47.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 64.1667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 20 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 40.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82850.2163 | 529 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42304.1663 | 550 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.2499 | 195 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 457.3 | 269 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1219.4998 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1736.9999 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2893.4998 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4119.6666 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14426.6666 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 20.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 32.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255 | 255 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1111 | 220 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11344.4998 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38933.95 | 319 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 93.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 48.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 55 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2559.3333 | 220 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3055.4998 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 656.5 | 130 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12948.4831 | 287 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 52.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 58 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 58.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26452.9666 | 347 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | SF-Startup Failure | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2300.5833 | 95 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7408 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3600.5 | 190 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 85.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 38.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 45.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 46.6667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 934.4332 | 289 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1917 | 270 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2812.5165 | 319 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5760 | 320 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 476.6666 | 130 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 68.3333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 485.3333 | 130 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 26.6667 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 30.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 35 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 162.8333 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 14368 | 32 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 156.8667 | 26 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 19224 | 27 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 280 | 35 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 240 | 30 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 355.2 | 36 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2862.6665 | 190 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 196.6666 | 118 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5961.3332 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.5 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4687.6666 | 245 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3600 | 320 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.5 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19929.6664 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 311.2 | 155.6 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1068.1666 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1237.5 | 110 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5200 | 400 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19555.6664 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1150.5 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45164.4999 | 354 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 821.4665 | 244 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 409.9998 | 300 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45939.6664 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19266.6664 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50008.3332 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 559.1666 | 110 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10625 | 340 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 106.5 | 21.3 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1939.4999 | 270 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 327 | 218 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 48 | 20 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 800-Miscellaneous
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1615.4999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 258 | 43 | 2 | 2 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 800 | 60 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1227.1665 | 398 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1087.9666 | 254 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7442.9998 | 540 | 2 | 2 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7891.3331 | 380 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28198.4264 | 354.4 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1841.7499 | 159 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5024.0498 | 267 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6825 | 195 | 1 | 1 | 0894-Bottom ash piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 697.4999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 32.5 | 13 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2685.3332 | 304 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 542.4666 | 206 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3721.2999 | 224.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 696.3 | 18 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3747.6 | 347 | 1 | 1 | 0894-Bottom ash piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5159 | 308 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8202.8331 | 395 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24441.7864 | 354.4 | 1 | 1 | 0894-Bottom ash piping and valves | U2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187 | 340 | 2 | 2 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.5 | 195 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3708.333 | 500 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4706.8332 | 310 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5219.9999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1602.7916 | 32.5 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 650-Fluidized Bed
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1368 | 304 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 519.7999 | 276 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9058.3999 | 201 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 274.1265 | 316.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5648.7165 | 377 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 522.6667 | 25.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1378.8 | 21.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 193.6 | 12.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1316.25 | 351 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1278.3332 | 236 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17132.8665 | 383 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1258.6998 | 246 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58146.6662 | 700 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37227.6 | 766 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41287.4 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 786.4999 | 165 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 107.7333 | 10.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 222.8833 | 8.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 317.675 | 9.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1412.55 | 219 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 683.1 | 207 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1618.4998 | 234 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 845.5 | 178 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11626.2998 | 357 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43125.4164 | 415 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32309.3331 | 416 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 363.3333 | 20 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 154.6667 | 11.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 213 | 9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2144.2 | 302 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1747.5666 | 206 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1087.2333 | 193 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1238.4 | 288 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2745.75 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44278.2195 | 736.13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9441.8695 | 816.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1490.9999 | 180 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1999.2 | 392 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 251.6967 | 9.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 420.75 | 8.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3405 | 454 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 585.9331 | 374 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3684.8 | 392 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2340.7998 | 264 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1526.25 | 275 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1104.7665 | 253 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1297.85 | 257 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 147.6065 | 316.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.8167 | 11 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 42.3 | 9.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 195.0417 | 15.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 842.9165 | 425 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1948.1998 | 306 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 460.1666 | 110 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 939.25 | 221 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1012.65 | 157 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5858.2 | 102 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 982.5999 | 204 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4021.6 | 457 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1043.1 | 171 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3283.566 | 104.13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1417.49 | 616.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12840.85 | 407 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10366.1665 | 410 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 347.2 | 31 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 862.6 | 454 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 468.3331 | 281 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 12656.0665 | 229 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 795.3999 | 246 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1556.25 | 249 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 153320 | 800 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45740.0097 | 816.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 581.6666 | 100 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1497.6 | 288 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 664.35 | 129 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.1333 | 28 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4484.8332 | 355 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 932.7166 | 191 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13107 | 340 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75285.0331 | 766 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55327.0662 | 634 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10521.0163 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16595.2297 | 437.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3972.15 | 291 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 877.2499 | 165 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6781.5 | 330 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34797.15 | 477 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 188.3333 | 11.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 380.5499 | 387 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 838 | 419 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1030.2 | 202 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 854.2666 | 172 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1718.2665 | 392 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2099.6 | 362 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5075.8 | 619 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12013.2145 | 816.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1104.5 | 30 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141914.4164 | 881 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 967.5 | 90 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1023.7333 | 88 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 516.75 | 45 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 413.7 | 42 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 42 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 204.25 | 95 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9343.1499 | 201 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48573.7 | 431 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1765.4499 | 201 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 804 | 201 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4148.76 | 215.52 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29914.632 | 141.24 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6043.4733 | 135.1 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20070.233 | 431 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 366.6 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 547.7333 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 767 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 541.6667 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 454.7833 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 689 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1280.5 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 503.5333 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 728 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 357.5 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 360.75 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 331.65 | 201 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.1833 | 47 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1297.8 | 216.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4046 | 289 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 136.0667 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 855.4997 | 435 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 985.5 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2531.25 | 405 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44800.6664 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.8667 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98 | 49 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 33 | 3.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 73.6 | 9.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 960.9997 | 465 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2102.6664 | 415 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1154.9998 | 315 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10679.9247 | 816.3 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2055.042 | 141.24 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.3167 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2281.04 | 285.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1564.3833 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2996.3332 | 445 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.75 | 35.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1916.6665 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194 | 97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2028 | 312 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 625 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1710.5 | 110 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2993.7 | 51 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 128.5167 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1254.7499 | 315 | 1 | 7 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21701.2499 | 405 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.8 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2720.9066 | 54.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 649.3666 | 161 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1323.9555 | 180.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1415.0052 | 16.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30025 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.8213 | 5.18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 663.6 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 15.5 | 6.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 892.4999 | 450 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2239.9997 | 525 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 939.7499 | 315 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1039.5304 | 260.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1235.3332 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1208.865 | 26.1 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.173 | 5.18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 459 | 51 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 845 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.8333 | 110 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1360 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2276.75 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 9033.0831 | 305 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 106.4 | 48 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 41763.75 | 525 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1458.9166 | 305 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 365.0833 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 55.25 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 208 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1708.1 | 19 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1258.8 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2522.3333 | 28 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1627.1666 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 172.25 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 49 | 4.9 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 23480.9665 | 376.7 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1362.3998 | 312 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1283.7333 | 58 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0971 | Flue gas-solids separator piping and valves | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1057.3333 | 32.5 | 1 | 1 | 0971-Flue gas-solids separator piping and valves | U1-Forced - Immediate | 650-Fluidized Bed
0980 | High pressure loop seal recirculation fans/blowers | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 3287.8716 | 346.7 | 1 | 1 | 0980-High pressure loop seal recirculation fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2649.8333 | 32.5 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 60.4 | 6 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 21600.8 | 268 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10281.6997 | 429 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5742.765 | 371.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 95297.4 | 108 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2145.5416 | 32.5 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2031.9333 | 58 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 142.9333 | 16 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 88261.3666 | 293 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2355.4133 | 24.4 | 1 | 1 | 0990-Refractory | U1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | SF | Startup Failure | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 27013.3333 | 160 | 1 | 1 | 0990-Refractory | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 866.2 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2823.4866 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2465.62 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 51105.0999 | 237 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 525.6 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 573 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 957.42 | 24.3 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2470.905 | 24.3 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 42293.1665 | 253 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1420.4867 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 871.4867 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 13370.5 | 242 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D3 | Forced - Postponed | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 27535.2 | 176 | 1 | 1 | 0991-Tube leaks | D3-Forced - Postponed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1670.18 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 544.2 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2054.0733 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 621 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 804 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3580.4167 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6212.115 | 28.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6882 | 222 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11856.48 | 29.06 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 228 | 76 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1286.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 885.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1007.5 | 155 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1599.9999 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1828.3 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4499.6 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21409.9998 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 581.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 408.96 | 12.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 809.1 | 12.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 204.3 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 324.9 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9102.083 | 425 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20335.35 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 42390.2264 | 788.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4578.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4765.0666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5227.1 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7097.5 | 425 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9326.95 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11737.06 | 175.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13568.75 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14067.9 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29481 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13561.6 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23500.98 | 493.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24690 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26109.0956 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54816.4199 | 303.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65036.25 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 67349.8 | 659 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3053.3166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4664 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6270 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7443.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13616.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17880.333 | 485 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40970.6832 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114733.6664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117131.105 | 557.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51126.1665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23234.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8371.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12924 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 85366.4499 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1798.5333 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 3814.05 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1821.25 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1623.3333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20043.4666 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22094.0499 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45635.772 | 206.31 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19110 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51221.5382 | 260.78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62292.8829 | 581 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 963.7 | 138 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36384 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93349.8662 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 28912.3759 | 335.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8852.9998 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37844.0132 | 354.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52590.5332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25807.5 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31160.5 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50302.8497 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 252 | 84 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 381.3333 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1343.0333 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1917.3 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2369.5 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6098.0666 | 194 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11053.75 | 185 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21323.6666 | 90.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.3333 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6651.05 | 30.65 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9312.5 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 631.6 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3972 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6998.3332 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11038.3 | 182 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 560.1833 | 12.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 309.75 | 11.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 958.5 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 92.4 | 154 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 82900 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5529.9997 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5346 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1702 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1948.3332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5069.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11820.6 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17272.4996 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30218.5832 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31135 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45607.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52842.5 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106360.9995 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192619.9328 | 812 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5449.5 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5785.4332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6654.75 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7344 | 102 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12380 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26017.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28560 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31616.7829 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38797.8331 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63393 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117314.3 | 1231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 412.05 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7105.85 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10530 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11212.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23236.3398 | 264.45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28560 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28860.25 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30001.95 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30740 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31626.3331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34451.1665 | 485 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135277.5 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 47129.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3306.25 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 25915.4 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 59798.2999 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1275.9999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3260.2332 | 416.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6385.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11976.85 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 31189.2999 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 5068.3664 | 397 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 12666.54 | 333.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 3179.3175 | 30.15 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11949.9332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5187.5 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20922.9164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28900.4332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35389.6664 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18509.25 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28842.65 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40217.5831 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 16932 | 498 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 317.3333 | 16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3269.55 | 46.05 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3482.9666 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11925.76 | 38.72 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16659.02 | 43.61 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 838 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2292.5 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4107.4666 | 146 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 821.975 | 23.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1033.5 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 425.68 | 425.68 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13223.925 | 29.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 183.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 7575.4635 | 78.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7489.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17462.5 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33165 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33936 | 707 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37835.505 | 816.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46417.6662 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51510 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97077.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154080.5 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285675 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3469.6999 | 102 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5285.1 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17376.2 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17959.0492 | 260.78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29744.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34809.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82149.9998 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95512.5 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4824 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7311.8166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11900.2 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12661.3832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16284 | 295 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23735.8329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30341.8995 | 723 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30425.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37565.1165 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39697.3994 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41115.6662 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45516.0832 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53926.5831 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61033.4 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 286393.3329 | 680 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 98569.8999 | 183 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9374.4 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11544.1665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 56542.7499 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 99715.6695 | 333.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6985.8666 | 136 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9509.9183 | 120.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16549.3332 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83352.7498 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9213.0499 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22962.7571 | 388.76 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4705.1499 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42920 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19234.7498 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2070.6666 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4210 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4290.2333 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15722.52 | 30.47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 901.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1441.6666 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1950.1999 | 294 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2295 | 675 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2677.5 | 765 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4422 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 29.625 | 2.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 403.56 | 10.62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 892.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 411 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 505.4333 | 11.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 875.7 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6520.7998 | 468 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 921.9166 | 185 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13665.8332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 999 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3417.9332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3630 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8401.4 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18335.1999 | 264.45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19857.5 | 611 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44214.75 | 645 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44270 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58125.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76929.75 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101725.1663 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110874 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132645.3329 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4462.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7240.9999 | 195 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7357.5332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9010.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9433.5999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10606.05 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11548.3332 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20220.6663 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25172.6663 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30438.3164 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39753.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41966.25 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60916.05 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69347.9 | 431 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69527.2331 | 347 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4815.1666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8872.0666 | 116 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31356 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37228.0998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37932.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52823.333 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92649.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135277.9996 | 1320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191272.4996 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 52894.4 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2739.1667 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5259.9998 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7338.5 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9047.1998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16029.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46429.2663 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109956 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18219.0998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47132.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 72063.2 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 625.3333 | 70 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1415.12 | 28.88 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1462.0833 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4064.76 | 32.26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5518.8 | 1022 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10377.3331 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 443.7 | 51 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2117.5 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 918.75 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 627.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 232.5 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3129.4166 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5104.6332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7820 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8149.05 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14854.1665 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30162.9832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38912.7246 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39304 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98280 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133112.1663 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11334.1666 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22483.1331 | 652 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23018.1812 | 260.78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31031.1833 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32249.9999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38221.0031 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38423.0833 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43769.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51062.4998 | 570 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67960.1332 | 472 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134788.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4660.6505 | 74.91 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5210.4 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8004.8666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9233.2 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23630.75 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45112.4991 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70380.75 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 28154.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24689.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 16036.8166 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 54277.5328 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3327.85 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3695.8333 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6391.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7342.5499 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 42741.6 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7986 | 363 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10202.1332 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25898.5998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38336.1996 | 591 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61944.25 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22523.4 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37929.7995 | 732 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75299.4 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34129.8 | 849 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50252.3331 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10380.4165 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23933.7 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20143.35 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24276.1 | 382 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1317.6 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1596 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3575.9995 | 720 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5426.2 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 724.2664 | 388 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9336.6 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 154.4 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3050.61 | 50.01 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 666.2418 | 34.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2260.7841 | 160.15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1595.8 | 23.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 354.7467 | 10.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 530.9333 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 263.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 351.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3839.3333 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1293.75 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14190 | 660 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 28492.1832 | 497.97 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4847 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5957 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6482.6664 | 442 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12321.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15659.1666 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18130.1665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24247.5 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24977.6332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29898.5119 | 390.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53087.4998 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112381.5 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9040.2332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10355.5 | 745 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11355.6665 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12389.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14380.9032 | 216.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15119.4 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19323.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23480.8 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25566.6666 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26438.5328 | 728 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37395.25 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37778.9996 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43116.5 | 254 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 47891 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52625.5329 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58316.9996 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19508.3832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27062.35 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36847.5 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43868.4997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65002.5 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69999.7997 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22591 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 40723.1498 | 335.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 71422.45 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3017.8333 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10752.4999 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32400.6666 | 212 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 49184.3328 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 120684.6333 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 18297.4997 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 113308 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2731.4833 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29524.6662 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12526.8 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39282.75 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 130436.55 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14618.7665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17390.4499 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13483.1666 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115352.1 | 486 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22956.2664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30940.65 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1625 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7840.7317 | 23.99 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24389.4733 | 81.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2810.1666 | 65 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3314.5 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7550.4 | 429 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9515.2 | 30.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12757.82 | 40.63 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14459.55 | 43.95 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93253.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 677.3241 | 48.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 587.375 | 12.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 326.55 | 15.55 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 810 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 953.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4959.9 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6590.9332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11528 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22821.0547 | 390.66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28927.1832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33179.2996 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41820 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5674.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9227.5999 | 102 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14483.7 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15590.1331 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25299.1163 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27044.3331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31773.8331 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57974.4998 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58506.9328 | 728 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68487.2621 | 810.82 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70707.3331 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75815.6663 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81169.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114447.6664 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5636.25 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19649.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31865.75 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56072.083 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83346.6658 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85410 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93171.2831 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111937.4991 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31652 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5108.8 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 20323.8 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 748.35 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 42817.8328 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 58714.5 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1793.05 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2665 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25775.6465 | 571.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9074.6533 | 171.76 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20415.9999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40462.4996 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58410 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 235740.9994 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54864 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71126.3331 | 790 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47138.9997 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13895.2178 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12968.55 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32081.3 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24755.0997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42403.1663 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 318.4666 | 34 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23577.36 | 31.69 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3525 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5823.36 | 26.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 285 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 222.3333 | 9.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 550.8 | 13.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 458.1667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6544.7999 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2901.0999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4127.7499 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9948.5166 | 269 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11561.9666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13211.9999 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13315.4666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14192.2166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14214.4832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14370.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16506.6666 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16662.4165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53374.9995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58356.9995 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59698.7397 | 816.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72377.1665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86941.9999 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88618 | 472 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6906 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8090.25 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9328.335 | 175.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17129.3332 | 354.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27908.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36317.6331 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45497.4165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52016.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76968.158 | 550.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1281.9333 | 82 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24162.1166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34968.2665 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56246.6658 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59774.7663 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 27180 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 27793.5 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1860.8333 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15443.3332 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 63982.9166 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 162 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6519 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9677.1999 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16681.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 26669.2999 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26711.5999 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 274872.5 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2573.25 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19479.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48671.6997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49163.5662 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44460 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 38417.9999 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4920.6666 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 11403.8666 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3900 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 25208.7497 | 525 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 6192.1 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 18898.5 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 13250 | 265 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 42183.75 | 525 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 2725.2333 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2072.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 325 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 459 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1413.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 727.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 704.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1632.4 | 28 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2565 | 57 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1371.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2000 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 2146.6783 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1059.1166 | 53 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2124.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1095 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1167.4667 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1241 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 443.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 977.0833 | 35 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 4896.395 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 755.1 | 54 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1137.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1386.7 | 28.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 527 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1379.4 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 378 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 625 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1698.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1079.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 279.5 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1563.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 695.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1651.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 9329.9332 | 349 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 7059.9999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 9246 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 19644.4 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 490.1667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 13053 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 55005.0664 | 746 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1835.25 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 28577.2832 | 349 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 726.55 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1915.45 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 2344.2 | 36 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 6584.4664 | 349 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 8266.9 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 935 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 27246.6665 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15093.8664 | 728 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8978.6664 | 728 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73587.4998 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95404.4 | 728 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 925.6467 | 17.2 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61498.8498 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5424.7533 | 171.76 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 69630 | 45 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1565.4 | 36 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 77.7307 | 16.48 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 529.5 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 583 | 22 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 816.3667 | 19 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11310.4166 | 61 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 912.6 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 988.9 | 22 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 175.75 | 19 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40751.5 | 745 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2454.9667 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65228.5331 | 601 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12476.485 | 135.1 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 59537.9162 | 745 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4834.5 | 99 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1966.95 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2122.8333 | 47 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1396.9999 | 330 | 1 | 1 | 1005-Generating tubes | SF-Startup Failure | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51477.6 | 241 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43545.25 | 745 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 0 | 0 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3173.0833 | 32.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2176.9583 | 32.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1300 | 32.5 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3552.4999 | 75 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 218.5 | 10 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.05 | 49 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4188.3333 | 70 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54126.6665 | 575 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52046.6663 | 592 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14914.9997 | 471 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 667.5 | 75 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64362.9163 | 565 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152305.65 | 497 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U3-Forced - Postponed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37718.1665 | 554 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2862 | 135 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93609.9998 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168.0999 | 246 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21070.5 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11546.5466 | 135.1 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 480 | 90 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1038 | 120 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3836.068 | 49.69 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35595 | 565 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34513.6 | 592 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21660.3766 | 813.79 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62820 | 600 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38034.7496 | 585 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15684.333 | 446 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10874.7 | 258 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1474.7499 | 255 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1312.8 | 547 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11631.6665 | 175 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14297.35 | 269 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21348.4241 | 813.79 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1375 | 100 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29880.8329 | 575 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 56466.4828 | 737 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27753.4 | 719 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67187.3329 | 620 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 558 | 20 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36761.3331 | 395 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12821.7331 | 296 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4270.1333 | 67 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35038.6666 | 176 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78249.9998 | 750 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14269.3666 | 197 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63854.55 | 491 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10233.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38412 | 528 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43535.3329 | 665 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2907.6666 | 143 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21785.8166 | 347 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 98247.8498 | 339 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 9722.2499 | 135 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75787.4664 | 472 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114205.9998 | 510 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27285.5 | 410 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44254.9663 | 493 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22767.3331 | 568 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33709.9998 | 600 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 6222.1499 | 81 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10657.0163 | 493 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14781.5 | 235 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50109.3328 | 860 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36713.5829 | 635 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77043.9998 | 660 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135174.9997 | 750 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18012.7 | 86 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4926.25 | 175 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91025.2 | 812 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5600 | 175 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45427.5 | 450 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10760.9999 | 180 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40020 | 580 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29640 | 600 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127530 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25316.6665 | 500 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94728.6665 | 530 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 48606.75 | 285 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 42971.6665 | 295 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 46314.25 | 305 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1596 | 285 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 58950.8332 | 295 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4385.6665 | 295 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 35341 | 295 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 829.9317 | 20.3 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 933 | 18 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1717.1 | 154 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30773.6664 | 860 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51600 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 179915.7997 | 876 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28358.3332 | 415 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58176.5829 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22521.6 | 153 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 27043.3332 | 427 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 4585.6333 | 47 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 253.145 | 9.85 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3649.5 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33978.75 | 425 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 47223.1663 | 595 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7187.1666 | 290 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8019.75 | 255 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61025.8331 | 670 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68665.483 | 431 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 113915.4997 | 411 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 4128.1667 | 47 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33274.5832 | 325 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52697.7163 | 607 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 67547.3331 | 610 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22948.3331 | 350 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6253.0665 | 262 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23191.5832 | 415 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 495.2348 | 228.57 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 309.4 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18258.9999 | 228 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34599.9996 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43618.8 | 446 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47867.4 | 812 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77112.4995 | 750 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78171.3332 | 245 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1697.3448 | 63.77 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 3590.0167 | 47 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12391.2 | 206.52 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15346.1165 | 223 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 49198.8663 | 577 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6602.4998 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21697.7997 | 387 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74893.2 | 417 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 39585 | 455 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45150 | 840 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 714.633 | 103.57 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 320.675 | 63.5 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1922.1492 | 13.85 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 61925.304 | 932.61 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23096.3999 | 342 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94947.8498 | 249 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15560.4165 | 175 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2559.15 | 47 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37363.8332 | 415 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6649.9998 | 600 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1500.0833 | 47 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 544.4266 | 127.6 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 814 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99745.9662 | 766 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78865.4998 | 630 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12075.8 | 132 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53056.2999 | 417 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21334.1332 | 176 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 32985.1663 | 577 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.4666 | 89 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8585.4 | 164 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11708.3999 | 198 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33134.85 | 471 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 134295.84 | 932.61 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10088.9998 | 270 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12258 | 270 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14377.9999 | 195 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9162 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21020.9996 | 630 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 3767.7441 | 63.77 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9098.4 | 223 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24240 | 600 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 44864.6331 | 658 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2765 | 70 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 3223.4167 | 47 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 414.3375 | 57.15 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10493.9333 | 199 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17913.7499 | 225 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87211.6664 | 710 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6137 | 38 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5407.9999 | 240 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17476.9332 | 164 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2003.62 | 42.6 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1793 | 22 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1221.7333 | 154 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1763.3 | 154 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1863.4 | 154 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1178.1 | 231 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11145.45 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29478.4 | 448 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3452.9333 | 47 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111897.0665 | 416 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18399.1998 | 654 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 41007.9998 | 330 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3861 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 583.2 | 24.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1117.8 | 24.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 290.7 | 32.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 468.3117 | 29.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 318.9783 | 13.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 19749.8332 | 355 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 22051.4164 | 355 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 351 | 27 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4260.75 | 741 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 297.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20141.25 | 393 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58554.1664 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87564.7498 | 585 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15828.2664 | 352 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29529 | 579 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70535.25 | 345 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 31487.4998 | 330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44691.2997 | 459 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 275764.6898 | 509.7 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2416.5833 | 47 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2173.5 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78555.7498 | 585 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19731.2498 | 231 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4158.3 | 167 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11991.985 | 120.1 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4231.7666 | 158 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 540 | 100 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3628.8 | 9.45 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1111.5 | 19 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1381.3332 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 931.7 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 33764.4998 | 330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43482.6665 | 620 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59239.9998 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94434.9997 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27600.129 | 390.66 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1036.1 | 39 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1940.9 | 39 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13581.9332 | 164 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 44359.3498 | 747 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1908 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37749.9996 | 600 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75009.4996 | 615 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102637.9994 | 876 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 282.3332 | 385 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2998.1533 | 13.1 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 803.25 | 7 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 914.5249 | 235.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2042.8333 | 7 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2873.898 | 23.83 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 528.6167 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 528.7333 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9306.5665 | 199 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34970.496 | 662.32 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 138255.1998 | 564 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32017.5329 | 644 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8166.73 | 571.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10156.0831 | 335 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 922.5 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34197.15 | 507 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51469.9998 | 600 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41623.75 | 497 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9114.2666 | 136 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2623.6666 | 68 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3468.1 | 158 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6275.2332 | 158 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 425.5333 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9201.871 | 24.51 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36604.5 | 345 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 648.9 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 452.55 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1273.65 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19514.2483 | 120.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36612.4996 | 606 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47747 | 665 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80949.9998 | 750 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98884.9331 | 712 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24990.8666 | 164 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18279.1665 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13751.2666 | 158 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28110 | 600 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79438.5 | 417 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15622.8332 | 245 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3784.2833 | 47 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1706.4 | 474 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.3333 | 19 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.6833 | 109 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 457.0667 | 32 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3930.4667 | 19 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 936.4833 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37683.0815 | 571.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71532.2662 | 712 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155175.1998 | 564 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8640 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9791.7666 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24079.9997 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 160488.0331 | 338 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2948.25 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30490.0829 | 593 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32427.4998 | 510 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6167.8666 | 167 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 86782.4995 | 675 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5039.4166 | 163 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3586.6 | 158 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 155.7833 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1806.1167 | 7 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1164.8 | 29.12 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1040.2 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 679.65 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 967 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29813.3329 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40957.5 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42499.1664 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121319.9991 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21511.2332 | 493 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33336.9997 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62288.1331 | 712 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93633.9496 | 579 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1953 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25239.9996 | 600 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30404.6665 | 590 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17548.2665 | 416 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37296.5831 | 595 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64215.4663 | 496 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21119 | 245 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32376.6332 | 469 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.9333 | 19 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 924 | 330 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.95 | 93 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1128.5 | 305 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1154.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 538.3 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1034 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13104.2999 | 198 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35377.4997 | 450 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61520.4497 | 471 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98211.3992 | 1239 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19558 | 120 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30808.5 | 690 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124218.3998 | 552 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1608.75 | 39 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 25117.9165 | 575 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2809.8167 | 47 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1778.25 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2439 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 690.75 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1857.75 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30832.0833 | 175 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 499.7 | 114 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3441.9499 | 219 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1796.6666 | 275 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 585.9333 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 874 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1652 | 24 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1582.35 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 420.7195 | 24.11 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57745.9997 | 780 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34024.6665 | 644 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34549.6664 | 340 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36609.4998 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56283.6 | 712 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3960.6832 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57307.7498 | 615 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67787.5 | 550 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12808.4 | 164 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46729.9998 | 600 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2641.3832 | 167 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29996.2497 | 855 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 490.8293 | 4.12 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 29857.3332 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 4045 | 37.5 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 87444.4999 | 330 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 467.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 986.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 530 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 938.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 4565.5 | 115 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1360.1816 | 25.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 409.5 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 683.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2495.465 | 25.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 617 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 364.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1661.1833 | 41 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 8654.6 | 218 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1790.3333 | 41 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 347 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 566.6667 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 192 | 64 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3510.5832 | 409 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 33101 | 419 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2423.2165 | 419 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 11070.2664 | 409 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 655.2 | 504 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5000.0665 | 419 | 1 | 1 | 1050-Second superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17810.6833 | 193 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2901.0999 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30637.35 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32927.6 | 626 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36784.2001 | 810.82 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54462.4995 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33346.5 | 705 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41477.75 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44162.7662 | 658 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47421.2664 | 662 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32442.6663 | 616 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33680.6665 | 380 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155828.4 | 728 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9644.25 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55107.3998 | 732 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17508.6 | 493.2 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 186.5 | 10 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15.5166 | 49 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35004.1665 | 271 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36945.6665 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39032.05 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60880.6663 | 580 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73919.7561 | 810.82 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99715.05 | 783 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 133458.6999 | 213 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8493.0998 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1157 | 260 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6180 | 103 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 51991.45 | 147 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26565 | 700 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35542.6665 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59656.6663 | 550 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1830.7996 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14845.3331 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33973.4498 | 339 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18956.6666 | 200 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 35598.3332 | 212 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23262.3331 | 380 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24000 | 600 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7105.85 | 167 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9031.5 | 270 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5053.3666 | 158 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19782.3831 | 293 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81337.3332 | 212 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48971.3331 | 580 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88670.4 | 416 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15431.3331 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31583.7662 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58315.8329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1723.3332 | 200 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36824.6625 | 264.45 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 84486.2662 | 691 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16799 | 107 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55625.5 | 691 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39978 | 120 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80322.9998 | 705 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24492.4773 | 264.45 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53374.9995 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7793.2164 | 469 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39929.9621 | 813.79 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56647.9994 | 876 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73268.0666 | 154 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4308.2498 | 285 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62598.6663 | 532 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80091 | 660 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89914 | 610 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 114961.7328 | 824 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24809.8173 | 264.45 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33469.9998 | 600 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38871.6664 | 415 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.7333 | 13 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 942.05 | 45.4 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16521.7499 | 189 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121887.4995 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8130.7332 | 262 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14512.4 | 568 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17603.3332 | 200 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25039.6665 | 220 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31347.2 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5916.6666 | 125 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5296.2 | 156 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8770.2998 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45686.6162 | 691 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87067.4998 | 585 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6650.7999 | 156 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 102382 | 824 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1073.4666 | 194 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7894.5 | 831 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 384.1833 | 37 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3173.8399 | 245.4 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69236.1665 | 635 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14146.3329 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21406.5 | 670 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43365.6 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30097.5331 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 33637.5 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25449.9996 | 600 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7688.4499 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10065.136 | 171.76 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 218386 | 1330 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9744.3499 | 231 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11015.9999 | 243 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35010.1665 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41903.3997 | 816.3 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45879.9996 | 555 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88145.75 | 241 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24407.6 | 644 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73012.5 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98756.6658 | 1300 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118783.1662 | 730 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4492.8 | 156 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97701.6665 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5980.1165 | 223 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67987.3329 | 635 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65099.0663 | 532 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 18218.5999 | 213 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 800-Miscellaneous
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630.7425 | 280.33 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32594.964 | 810.82 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28800 | 300 | 2 | 2 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11179.7666 | 218 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24450 | 600 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13546.5 | 330 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21932.3331 | 380 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54578.9163 | 535 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80339.9994 | 900 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30630 | 600 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26100 | 300 | 2 | 2 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18753 | 380 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50067.25 | 739 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45982.2496 | 579 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121862.4998 | 750 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 76061.6332 | 523 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6380 | 176 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22798.0831 | 395 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3139.5 | 390 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5472.9999 | 390 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11174 | 151 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10721 | 151 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61670.4 | 876 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20234 | 151 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15207.4999 | 330 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19493.25 | 395 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99300 | 300 | 2 | 2 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 38844 | 390 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12270.4999 | 330 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259971.7 | 634 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 358.3998 | 336 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85740 | 600 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25398 | 510 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 18725.8329 | 575 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1221.6667 | 20 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 800-Miscellaneous
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2615.7333 | 68 | 1 | 1 | 1075-External reheater link tubing | U2-Forced - Delayed | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 681538.6663 | 580 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 309.6667 | 10 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 526.5 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 682.2 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73162.5829 | 635 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17137.9999 | 285 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17148.6666 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4999.5832 | 355 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8040.9998 | 330 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12305.6666 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29369.5999 | 192 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 6381.6667 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2985.8333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 4164.1667 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14209.9998 | 600 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88257.3328 | 740 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 143903.4664 | 836 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 928.2 | 14 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7872 | 164 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21357.9 | 342 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 536.5 | 58 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 629 | 37 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35509.9998 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 9279.9166 | 95 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8724.1666 | 95 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 85 | 51 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2508.2333 | 47 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 183.75 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 101 | 10 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21878.9999 | 270 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7959.4166 | 95 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18192 | 758 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 21154.1665 | 250 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 94370.4664 | 836 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 553.41 | 111.8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 678.5 | 69 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3193.6667 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31740.8998 | 558 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145803.9 | 1243 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1654.5831 | 275 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6978.6666 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16214.5998 | 228 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 79245 | 675 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8925.25 | 95 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13813.2 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 894.6667 | 44 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1898.3333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 5430.1833 | 43 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3639.1667 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15607.0833 | 175 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25197 | 740 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 11666.6665 | 250 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3080.7666 | 58 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4167.8 | 42 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 45.99 | 4.2 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 951.1833 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2494 | 58 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6858.0833 | 235 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7612.5 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20257.2 | 662 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50667.5 | 650 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 59940.8329 | 650 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63825.9996 | 564 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66174.6896 | 813.79 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2029.225 | 47.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3699 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5471.9999 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12379.5 | 315 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19659.3328 | 740 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 43439.6 | 524 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1593.0666 | 58 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19345.8996 | 609 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 521.7333 | 14 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1559.75 | 15 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81273.5 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38351.9998 | 576 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53935 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14053.4997 | 486 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97544.3328 | 740 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4329.275 | 47.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33218.3331 | 380 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 777.924 | 52.92 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2064.6665 | 380 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 257.5 | 10 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 29733.4332 | 427 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 14965.6665 | 190 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3111.6667 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13547.9165 | 175 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78773 | 740 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 17325 | 250 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58642.8662 | 691 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8254.4 | 112 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 735.4417 | 11.3 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13272.7497 | 459 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99081.6658 | 1300 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 264.0917 | 47.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6993.305 | 47.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 924 | 44 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3178.3333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17622 | 135 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2538.4 | 167 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 162253.6664 | 836 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 487.512 | 3.66 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1221.875 | 37.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 467.3913 | 5.54 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1505.385 | 24.3 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 534.4 | 6.4 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 2640.625 | 37.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 884.115 | 24.3 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1746.25 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 363.35 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 387 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 567.6667 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 396.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 611.3166 | 43 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 177.6667 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1786.7 | 51 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 21079.6 | 349 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 20974.3331 | 356 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 9213.6 | 349 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 10590.8332 | 355 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 30374.6332 | 349 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 11468.115 | 78.9 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 16749.155 | 78.9 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 331.2 | 7.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9563.4 | 231 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9973.2832 | 179 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 26690 | 785 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 82398.6499 | 411 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 7108.4 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 27753.3 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27336.9063 | 548.2 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9010.283 | 539 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10144.1665 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126102.0664 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1882.9333 | 46 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | TRE | Summer | 3082.8 | 7.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73501.9997 | 780 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91895.0829 | 635 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1863.3333 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63581.6163 | 619 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11043.1333 | 151 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16027.7831 | 553 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19532.9332 | 472 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 35331.8331 | 598 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 45714.6 | 654 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8217.45 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30256 | 244 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 144937.1664 | 785 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34615.1665 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1449.0442 | 20.29 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 261.7997 | 462 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2020 | 60 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12096.6998 | 462 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 621.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70034.9996 | 630 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97983.0662 | 712 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12590.9972 | 176.18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 142856 | 560 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 14392.35 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34679.5164 | 427 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7294.1667 | 25 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9802.2 | 93 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10893.6 | 68 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 2422.1971 | 63.77 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 20569.05 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 398043.3995 | 762 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 707.7 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 109495.8665 | 536 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 410.3239 | 161.97 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 432 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18454.3999 | 192 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17405.85 | 363 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25334.9999 | 270 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40311.6997 | 429 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48140.9331 | 589 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193240.6666 | 260 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 11737.06 | 127.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 52332.9164 | 355 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10001.3333 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 27341.5415 | 182.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16186.833 | 492.5 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 69897.3997 | 411 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54 | 9 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1341.25 | 111 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1814.5 | 38 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25640.1832 | 269 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21705.6666 | 260 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 16538.85 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 34901.0666 | 112 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9746.5333 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21630.2666 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 72140.2662 | 736 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 146553.833 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95507.3 | 602 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.9 | 9 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21471.2664 | 836 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1900.8333 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15846.6 | 231 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72814.5 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 136341.4164 | 785 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44880 | 176 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18900.75 | 435 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30146.2 | 353 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3024.3333 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21855 | 705 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 816 | 320 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3850 | 110 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7289.5432 | 216.2 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43890 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9933.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35060.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91499.1999 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7071.515 | 127.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9269.8666 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 109603.6664 | 749 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 11174.9999 | 90 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 15974.5 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36368.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12635.333 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1410.5 | 130 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 651.053 | 16.42 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31359.4996 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88470.9 | 453 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4352.4 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13247.55 | 81 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1693.0935 | 63.77 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 11757.0623 | 63.77 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33787.3932 | 548.2 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1135.2 | 18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 7864.0833 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 85536 | 330 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 5994.0833 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2019 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1817.64 | 24.3 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 6811.6663 | 610 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2019 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 439.0833 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 698.5667 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1069.3833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1398.3 | 39.5 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1016.1833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1174.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 437 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 794.5167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1459.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 535.8 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 357.2 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1268.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 699.3333 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1554.8333 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 548.15 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 655.8167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 710.9167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 753.9833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 816.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 658.9833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1095 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 788 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1080.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 491.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2802.1 | 42 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 47.5 | 38 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3643.9166 | 59.9 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5739.9999 | 150 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3054.9999 | 150 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3466.08 | 41.76 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 344 | 344 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2254.4666 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.2 | 12 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11476 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3807.9999 | 168 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10721 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11346 | 122 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 29316.7 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 44417.4833 | 107 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19194.5833 | 175 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1687.8166 | 119 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1898.7499 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1032 | 344 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8266 | 41.33 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1.2 | 2 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1314.4999 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6474.6663 | 607 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5587 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22952 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 74017.3999 | 183 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1845.3331 | 320 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5100 | 340 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8198.25 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255 | 42.5 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 630.6666 | 344 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4979.04 | 40.48 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6644 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9966 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.9998 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7858.8 | 70.8 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 483.45 | 322.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8154 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50434 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 6037.2664 | 761 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.5 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 688 | 344 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2274.8 | 41.36 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12678.25 | 235 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15100 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 32287.5333 | 68 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 337653.3 | 183 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5134 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 507.15 | 24.15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 516 | 344 | 1 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2763.18 | 43.86 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4228 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 608.1166 | 107 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47829.3331 | 320 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16524 | 68 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 47788.05 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22499 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1439.6666 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5637.8666 | 341 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2064 | 344 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 321.7333 | 19 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 25937.7 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 20791.6999 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11325 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 860 | 344 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4228.95 | 363 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 887.68 | 4.8 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3624 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9060 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11362.75 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29143 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36807.2666 | 68 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8154 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1441 | 22 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29401.1663 | 553 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 514.8 | 6.6 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53155.5498 | 609 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | NULL | NULL | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3041.7 | 18 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1103 | Steam generating tubes between steam drum and mud drum | NULL | NULL | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 193.7833 | 15.1 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 977.5 | 23 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4838.3333 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 18600 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 18000 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 10225 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 18600 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1999.3333 | 40 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3102.75 | 105 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21225.0814 | 736.13 | 1 | 1 | 1120-Convection pass wall | U1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3989.2498 | 243 | 1 | 1 | 1120-Convection pass wall | U3-Forced - Postponed | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.6666 | 31 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12301.5165 | 199 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13964.9996 | 630 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 2 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4140.99 | 28.17 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.5 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2071.2 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2814.5167 | 47 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1850.2333 | 47 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1954.4167 | 47 | 1 | 1 | 1140-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 799.5 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1964.75 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2597.4667 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 700.8499 | 321 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1930.8 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21 | 5.25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1365.2833 | 11 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1560 | 65 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 651.1 | 17 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31747.7665 | 446 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 335.1 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3000 | 125 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 433.3333 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 694.8333 | 55 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10973.0776 | 176.18 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 5.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.5 | 35 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1560 | 60 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4790 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9130 | 55 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101 | 50.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1597.5 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2325.7167 | 47 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28 | 7 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.15 | 21 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1274.6666 | 320 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1360.3333 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4878.75 | 75 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22801 | 151 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30351 | 151 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3759.1667 | 13 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4089.5 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1252.5 | 18 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 3.5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2902.5 | 15 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4521.6 | 9 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 2 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4363.5667 | 14 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 892 | 446 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.3333 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 618.3333 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2004 | 167 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.4167 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.4667 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4159.1666 | 230 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1297.9999 | 330 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63932.6661 | 820 | 1 | 1 | 1150-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.5 | 210 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1554 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4219.9999 | 240 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15946.5833 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 679.25 | 55 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 772.5 | 75 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1925 | 275 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146.1333 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1528.3333 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1983.3332 | 200 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2448 | 34 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 758.1 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4161.0662 | 664 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.3333 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.9999 | 120 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1368 | 171 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4608 | 64 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 965.3333 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1437.8667 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1632 | 34 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3264 | 34 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 832.5 | 370 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.3332 | 140 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.9999 | 90 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 300 | 50 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 964 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2806.25 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2061.1333 | 172 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6144 | 64 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.2 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 736 | 138 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1536 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3072 | 32 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 853.7333 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2631.1998 | 528 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178.75 | 55 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2338 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2903.75 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4410 | 45 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2298.3332 | 394 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56802.6329 | 611 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.25 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3469.9998 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5 | 5 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 475 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1245 | 45 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 425 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 481.25 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 597.6667 | 22 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 489.3103 | 121.82 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 913.3667 | 22 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8604.1665 | 295 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3716.5832 | 433 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.6666 | 100 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 341.25 | 105 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 520.5 | 45 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 537.5 | 25 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4280.25 | 65 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6840 | 60 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 748.6 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 810.35 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2556.4498 | 513 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469.3333 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2914.9998 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5620.75 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 541.6667 | 20 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4680 | 65 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.8667 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 621.8667 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 960 | 32 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2520 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.99 | 5.33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.99 | 1.47 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.99 | 9.57 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133.3333 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 224 | 8 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.04 | 8.18 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 489.25 | 19 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.11 | 2.57 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18660.3982 | 176.18 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.75 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 262 | 131 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 621.8333 | 35 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2296.4 | 24 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4980.15 | 217 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.5 | 21 | 1 | 2 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1823.05 | 14.44 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 703.5 | 210 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 950.4666 | 269 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 387.8333 | 130 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65830.3664 | 842 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.5 | 38 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 633.6 | 33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 3 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21.6667 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.99 | 10.33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 372.75 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1281 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1132 | 283 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.6833 | 37 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 547.8 | 33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3830 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.3333 | 22 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 230 | 23 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 338.8333 | 19 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7029.4166 | 67 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.4667 | 26 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 141.8333 | 115 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.5 | 25 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 756 | 112 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2345.2 | 33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 2 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 4 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.02 | 10.86 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288 | 8 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 396.06 | 8.61 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 422.79 | 8.29 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 801.4166 | 163 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1958.6665 | 208 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 387.8333 | 130 | 1 | 3 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 316.05 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 9 | 1 | 3 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 8 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.98 | 5.83 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.91 | 2.89 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.96 | 3.88 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112 | 8 | 1 | 2 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234.6667 | 22 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1275 | 68 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 506.1 | 12.05 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 844.6665 | 181 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32542 | 307 | 1 | 1 | 1160-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 750.25 | 15 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2156.7 | 26 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6236.45 | 33 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47 | 11.75 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 398.25 | 9 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.236 | 11.18 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.5 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2013.8333 | 43 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4861.2667 | 11 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.9 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.6667 | 23 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.05 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.5 | 23 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 349.6667 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1899.7 | 242 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1023 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1435 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 648 | 160 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6506.6666 | 305 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 30 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.1667 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.0332 | 137 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.6666 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 294.25 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27166 | 340 | 1 | 1 | 1170-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.5833 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.5833 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 578.4166 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1422 | 316 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.75 | 35 | 1 | 2 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 680.1667 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.6666 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.6167 | 19 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 196.1666 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1012.9166 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.75 | 55 | 1 | 3 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.25 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.0833 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 304.3333 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1798.5332 | 328 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414.1 | 41 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4041.4998 | 354 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2156 | 40 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1275.75 | 35 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2754.0333 | 58 | 1 | 1 | 1180-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.25 | 85 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 50 | 1 | 1 | 1180-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 50 | 1 | 1 | 1180-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6667 | 10 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.8333 | 25 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 931.6667 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.8333 | 10 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 626.5 | 35 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6666 | 65 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 80 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.9999 | 75 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.3333 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.9999 | 120 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487 | 60 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 762.5333 | 38 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.5 | 10 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 550 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.6667 | 2 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 467.25 | 45 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9677.5 | 35 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1113.3333 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 30 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.6666 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 25 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.5 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.66664 | 40 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.4167 | 25 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.5 | 30 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.2666 | 28 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1124.5 | 26 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1515.8333 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.5 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3452.8 | 48 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5512 | 53 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 256.6666 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 108.75 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 126.75 | 39 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 250 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 766.6666 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3276.75 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189 | 27 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 248 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 13233.75 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2626.5 | 255 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 577.9167 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1526.5 | 43 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6616.8331 | 290 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 167.5 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.9833 | 101 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 493.9666 | 73 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9573.75 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 158.5 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5091.1666 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 767.6 | 152 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 822.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 442.75 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168.35 | 91 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2420 | 60 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 195 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 543.6666 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 37.05 | 5.7 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 189 | 7 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 319.1667 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2196.25 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1847.9 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.5 | 10 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 554.7166 | 83 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4200 | 600 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 12 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1196.6666 | 200 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8375 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 16.75 | 6.7 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 394.4 | 87 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1755.6666 | 46 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1887 | 740 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 857.3875 | 3.39 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 217.3383 | 1.3 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 679.563 | 1.62 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 836.4 | 102 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U1-Forced - Immediate | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1770 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 117.3 | 102 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U1-Forced - Immediate | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1442.5 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3084 | 514 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 861.3 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12180 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2597 | 15 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1135 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1358.2166 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2648.3332 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6298.5 | 51 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 401.6667 | 50 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11532 | 62 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555 | 92.5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1112.3 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2724 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1999.7832 | 427 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | U2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3696 | 44 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7344.4 | 42 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.0833 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1166 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.5 | 15 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1362 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2947.2166 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12480 | 52 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1740 | 60 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1131.2166 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 496.1667 | 10 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 825 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2976 | 62 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5952 | 62 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7560 | 63 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 780 | 65 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9744 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1362 | 227 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1388.4832 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1816 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2866.5 | 63 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19344 | 62 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.5 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3585.7 | 69 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4032 | 48 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4082 | 65 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1359.4 | 42 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2095 | 100 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 6873.8165 | 229 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 760.45 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 908 | 227 | 1 | 3 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 536.1667 | 10 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4992 | 52 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.3333 | 40 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6048 | 63 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9402.75 | 63 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1362 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 947.2 | 37 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3060 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 925.1664 | 427 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | U2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 140 | 14 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 548 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 125.7667 | 14 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 41 | 6 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 959 | 7 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | SERC | Summer | 1227.4167 | 13 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 650-Fluidized Bed
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 1260 | 42 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 851-CC GT units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1230 | 41 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 852-CC steam units
1310 | Water side cleaning (acid cleaning) | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50013.333 | 440 | 1 | 1 | 1310-Water side cleaning (acid cleaning) | U2-Forced - Delayed | 100-Fossil-Steam
1320 | Tube supports/attachments | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 8385.2533 | 81.2 | 1 | 1 | 1320-Tube supports/attachments | D1-Forced - Immediate | 852-CC steam units
1320 | Tube supports/attachments | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 1797.75 | 51 | 1 | 1 | 1320-Tube supports/attachments | U1-Forced - Immediate | 860-Co-generator Block
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 870 | 600 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1330 | Slag fall damage | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 906.6664 | 340 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2213.8818 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 63984 | 86 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9168.4666 | 284 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13003.3333 | 25 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 19257.1666 | 113.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.6667 | 44 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 279263 | 97 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45804.5499 | 363 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | WECC | Summer | 350.2332 | 266 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1830 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4327.7666 | 74 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 1362.8332 | 370 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 73.8 | 41 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 852-CC steam units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 2864.5 | 51 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 1930.35 | 51 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 860-Co-generator Block
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15461.25 | 589 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 95687.6497 | 411 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5163.4999 | 138 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9724.0498 | 243 | 1 | 1 | 1360-Boiler drains system | U2-Forced - Delayed | 100-Fossil-Steam
1360 | Boiler drains system | NULL | NULL | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 10210.8 | 268 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1360 | Boiler drains system | NULL | NULL | SF | Startup Failure | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2331 | 518 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
1360 | Boiler drains system | NULL | NULL | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1479.6 | 411 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 14635.6666 | 332 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 109.35 | 243 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 949 | 146 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 2078.2666 | 143 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1651 | 254 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 4284 | 51 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 860-Co-generator Block
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.1666 | 110 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21799.1333 | 97 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180.5833 | 55 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2128.6666 | 248 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4215 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13452.9998 | 330 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1524 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 53.85 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8316 | 396 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 170.215 | 57.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5195.0833 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1584 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 91872 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 59142.6 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8439.9996 | 600 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6890.4 | 176 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 73.7833 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1545.8331 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13449.9999 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4659.3333 | 145 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10655.5 | 422 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 43.125 | 7.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 40 | 80 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2887.4999 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4080 | 170 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6261.1 | 58 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7208 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28032.9 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 80486.6664 | 400 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75 | 25 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 433.1663 | 565 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2185.45 | 401 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.9165 | 205 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 805.9331 | 314 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1186.4998 | 630 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3436.7667 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 333.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64240.0866 | 287.9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 371.64 | 11.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10775.9999 | 180 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 41398.4999 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 571.55 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1625.95 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1656.5999 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12412.9166 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 116.3749 | 199.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3259.67 | 69.9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3711.6664 | 340 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.05 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.5333 | 32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1829.25 | 135 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15413.2666 | 82 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 149.7833 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 619.3998 | 228 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2285.2331 | 383 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.3333 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 117.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 817.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 927.6 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 33.3333 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16869.0666 | 112 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 320.25 | 45 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2162.5 | 75 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2910.9 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5198.1833 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5230.2166 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 16617.85 | 163 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 584722.1666 | 290 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23912.4997 | 750 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1779.3332 | 340 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 38.3332 | 230 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 211.2 | 528 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9291.6665 | 500 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.8331 | 338 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 618.75 | 225 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3780 | 120 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 796.9499 | 297 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 50.215 | 8.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1235.7665 | 566 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1888.6832 | 379 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3923.05 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8470.75 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 765 | 153 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1471.3333 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6458.3332 | 310 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 23532.1333 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 4749.5 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3 | 15 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 86922 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4583.7164 | 707 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1828.5 | 530 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7300.3333 | 110 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 64024.77 | 146.7 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.05 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 319.7 | 278 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1115 | 223 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2384.4 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4725 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 113.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 702 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 820.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1123.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5984.5832 | 265 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10693.9999 | 120 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13.3333 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 249.3998 | 516 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4752 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 37094.5166 | 109 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 143794.1999 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.4 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 133.75 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 140 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 795.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2411.3833 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4828 | 68 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 36635.85 | 153 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 45355.1999 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 96984.1333 | 157 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 194.6999 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 237662.6999 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108715 | 85 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.1 | 243 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.05 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6807.5 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0.33333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.8667 | 38 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 161.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7658.8 | 82 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20617.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 371.4833 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5392.5 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17400.8333 | 157 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 6121.4666 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5382.9997 | 420 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 17338.1999 | 198 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 472.5 | 54 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8409.6 | 876 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3325 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4037.9498 | 249 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12723.6665 | 380 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248 | 124 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1906 | 120 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9046.8664 | 388 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 321570.6665 | 214 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 286.0667 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1282.2 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32.5 | 65 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 218.1665 | 187 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 291.3333 | 92 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 398.35 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 520 | 65 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7173.15 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 55032.2333 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.9997 | 420 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 893.75 | 325 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 11586.25 | 575 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 45.4333 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 87.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.6666 | 100 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 60 | 48 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 364.55 | 69 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6428.9163 | 535 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.1 | 211 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 55.5 | 185 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 71.9333 | 83 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1408.3333 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8225.25 | 55 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 200.9833 | 31 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 855 | 180 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.7331 | 362 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3586.7 | 78 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 40.8 | 51 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 466.6667 | 20 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7985.25 | 585 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16616.5998 | 546 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.8 | 429 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3353.9664 | 421 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.0167 | 19 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 367.5 | 175 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.1 | 51 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.0667 | 11 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 107.5 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 19005.6666 | 335 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2475 | 150 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 307.9998 | 528 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765.3333 | 80 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 90.1333 | 104 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13500 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 16.8667 | 11 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 470.6833 | 31 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2039.8 | 434 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 264.1766 | 96.65 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.55 | 21 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450 | 180 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4454.1833 | 37 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 268.8 | 128 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1010.6666 | 160 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1451.2499 | 81 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5565 | 700 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78338.6332 | 469 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2467.8331 | 335 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 279.5 | 86 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121.6666 | 100 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 65.1 | 18 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 292.2166 | 89 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 101 | 101 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 262.5 | 250 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6181.1 | 226 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | TRE | Winter | 4555 | 100 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | NULL | NULL | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 6.3 | 42 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 852-CC steam units
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2088.1666 | 335 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8416 | 320 | 1 | 1 | 1407-Forced draft fan lubrication system | SF-Startup Failure | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1751.5999 | 348 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 889.0332 | 358 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2047.033 | 434 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 279 | 124 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40119.7333 | 104 | 1 | 1 | 1407-Forced draft fan lubrication system | U2-Forced - Delayed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8991.21 | 280.1 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1804.9998 | 228 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3648 | 304 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21379.2 | 544 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300.2999 | 234 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1344.7998 | 492 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 268 | 335 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6233.3332 | 250 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 839.55 | 193 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47022.7332 | 322 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244890.2499 | 165 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428.3333 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.4331 | 326 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19311.36 | 90.24 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 51.5416 | 123.7 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 120.8333 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 151.2 | 27 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35686.6666 | 106 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2886.1 | 93.1 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 445.7853 | 22.16 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10598.7497 | 417 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39425.4 | 378 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56653.3666 | 326 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2868.9998 | 570 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.9999 | 183 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14584.5 | 315 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 542.5332 | 250.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 22.05 | 21 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 182 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 408.5 | 190 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1406.1 | 43 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5778.35 | 163 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2776.6666 | 170 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 995.5332 | 218 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5716.9332 | 212 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1184.1666 | 98 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10605.8332 | 286 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 613.48 | 250.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 980 | 42 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8240.9732 | 300.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81145.9999 | 312 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1322.58 | 13.16 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 786.6 | 38 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1465.2 | 296 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17294.7498 | 627 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2817.2499 | 177 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0 | 0 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6285.8333 | 190 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 681.5666 | 161 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 124.2 | 81 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 91114.2999 | 213 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 63580.2399 | 200.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 45833.5433 | 67.3 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 123.75 | 27 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 149.21 | 34.7 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 205 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 931.5 | 103.5 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5890.9998 | 645 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2100.8 | 416 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14121.5199 | 200.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 47.5333 | 23 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 323.9 | 158 | 1 | 1 | 1410-Forced draft fan motors | U2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4452.8574 | 206.31 | 1 | 1 | 1410-Forced draft fan motors | U3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2286.25 | 155 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 22528.4133 | 66.4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 211.25 | 13 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 800-Miscellaneous
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 365.0617 | 20.3 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 800-Miscellaneous
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 13621.3333 | 80 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35 | 30 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D3-Forced - Postponed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1079.6498 | 453 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2710.4498 | 453 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 109.5 | 30 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10175 | 110 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8293.3332 | 400 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1362.4499 | 279 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 269.5 | 30 | 1 | 2 | 1411-Forced draft fan motors - variable speed | D3-Forced - Postponed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1136.8 | 56 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57.6667 | 20 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D3-Forced - Postponed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3322.9166 | 275 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1664.5998 | 492 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2538.1666 | 314 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 243.9998 | 240 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1000 | 125 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1868.6166 | 191 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 437.4 | 243 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 120 | 240 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3820.84 | 64.76 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9.3333 | 14 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 427.5 | 50 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.6666 | 110 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.9667 | 23 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2950.2666 | 203 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1215 | 81 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 480.1309 | 236.13 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1551.9998 | 240 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1645.8998 | 453 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20863.3331 | 550 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.5833 | 7 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 11293.75 | 325 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 529.7466 | 26.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 862-CoG steam units
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 320.7066 | 26.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 862-CoG steam units
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4680 | 45 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5226.4166 | 59 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32629.9269 | 380.82 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8625 | 276 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21536.4332 | 322 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 216 | 54 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18 | 4 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.2833 | 37 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3255.36 | 271.28 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1940.363 | 247.18 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4794.9667 | 38 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1000 | 250 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.8333 | 25 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 258.5333 | 28 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23.1667 | 2 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 625.2166 | 161 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1558.9333 | 37 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55 | 60 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2636 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 954.8166 | 59 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 901.9165 | 395 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 359.45 | 79 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.85 | 39 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 266.5 | 13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 510.05 | 101 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5.8 | 3 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16.8667 | 44 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 495.9998 | 480 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1312.7166 | 79 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2215.2 | 39 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3169.8332 | 418 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 84.5 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 174.2 | 13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 517.7499 | 327 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345.6 | 256 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1170 | 390 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.1333 | 13 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 254.1 | 77 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1.4 | 12 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 1784.8149 | 398.1 | 1 | 1 | 1415-Forced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 867.6665 | 380 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 59.5333 | 38 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 242.7333 | 44 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1113.45 | 39 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1771.6833 | 37 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2851.9999 | 240 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8409.05 | 39 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 24.75 | 3 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1405.0665 | 479 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3640 | 160 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7328.75 | 533 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8308.2996 | 546 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28286.25 | 285 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 107.3333 | 70 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 67.3666 | 86 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 64.05 | 63 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186.6667 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 732 | 60 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 904 | 452 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 594 | 18 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 86.2832 | 167 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 144.4 | 19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 268.2333 | 26 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.9167 | 7 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.6667 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 755.4166 | 175 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.6666 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2205 | 245 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 748.1666 | 335 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1192.3332 | 511 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1349.01 | 149.89 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2711.9999 | 180 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 5193.7832 | 398.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8.2 | 4 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30 | 4 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 326.6666 | 200 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 120 | 20 | 1 | 2 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1198.9999 | 330 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2445.6665 | 220 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2523.3333 | 50 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.5 | 18 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.25 | 3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 44.35 | 3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60.1333 | 8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 470 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 672 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2952 | 12 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3509.3333 | 32 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8930.25 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 42831.0499 | 177 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 383.833 | 470 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1078 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 120 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 189.5833 | 175 | 1 | 1 | 1420-Other forced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 332.7999 | 156 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 511.3332 | 520 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.3833 | 49 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.9166 | 203 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37.0667 | 8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23763.2 | 12 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 250.6665 | 470 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 452.7667 | 47 | 1 | 1 | 1420-Other forced draft fan problems | U3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.6667 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 569.5 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 922.1333 | 38 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 527.65 | 173 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10.35 | 9 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 163.4 | 19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 231.7 | 21 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2006.2 | 21 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.9999 | 240 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4316.1665 | 470 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4726.8331 | 790 | 1 | 1 | 1420-Other forced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1593.7664 | 349 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 752.6666 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 405.7332 | 358 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 797 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 835.25 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2478 | 90 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1028.4997 | 510 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 49026.7164 | 427 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 271.95 | 49 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576.2 | 43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8123.5 | 422 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 110.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 118.4167 | 35 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21495 | 15 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7599.033 | 554 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22060.5 | 770 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 121.5 | 24.3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 582.795 | 24.3 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 4261.3333 | 160 | 1 | 1 | 1420-Other forced draft fan problems | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3602.4998 | 330 | 1 | 1 | 1421-Secondary air fans/blowers | D2-Forced - Delayed | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 115.8 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 42 | 5.6 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 480 | 128 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1802.781 | 15.69 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 3014.0833 | 35 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 304.5 | 20.3 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 3754.7167 | 19 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 202916.25 | 255 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204 | 30 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 324.3 | 47 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | U1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1005 | 300 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.75 | 145 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 516 | 172 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.4167 | 25 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 985.8331 | 350 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1537.2499 | 165 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16233.3333 | 40 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 282 | 94 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 22840 | 15 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.3333 | 85 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1657.9165 | 575 | 1 | 1 | 1431-Air supply dampers from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2425.065 | 127.3 | 1 | 1 | 1431-Air supply dampers from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.07 | 25.1 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.3332 | 164 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 83 | 83 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 113.6833 | 19 | 1 | 1 | 1431-Air supply dampers from FD fan | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2960.1499 | 219 | 1 | 1 | 1431-Air supply dampers from FD fan | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 427588.9349 | 146.7 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.0833 | 41 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 28113.6666 | 230 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30739.1996 | 576 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340.95 | 22.73 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 91.8 | 91.8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 272.8 | 49.6 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2764.1666 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3720 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2653.3333 | 160 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2288 | 160 | 1 | 1 | 1432-Air supply duct expansion joints | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 9736 | 160 | 1 | 1 | 1432-Air supply duct expansion joints | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 5345.3333 | 80 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.25 | 115 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860 | 80 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 497.8 | 524 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 273.4832 | 269 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 154.1333 | 32 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 986.65 | 21 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1449.0665 | 304 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 618.8 | 62.4 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135 | 90 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1279.25 | 301 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 119.5166 | 71 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 56.2333 | 14 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 879.7999 | 249 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 620.94 | 39.3 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 800-Miscellaneous
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.85 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.4 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.95 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.05 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 237.8 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.6333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 490.2 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.6 | 83 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.1167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193.7 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.5167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.5 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.6667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 252 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.25 | 45 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.7832 | 397 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 360 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 864 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 950.0333 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12319.6167 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 299.3333 | 40 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.2167 | 19 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130.65 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171.15 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.6667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.1333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 580.0667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 650.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.3667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.2 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.9333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.4833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.55 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 241.5 | 14 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.3667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 530.6167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1657.9333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1679.8 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.8333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 141 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.1 | 262 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.3333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 290 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 524.7833 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 736.95 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11537 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4720.3332 | 340 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3102.5 | 730 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406.6999 | 249 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 172.35 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.55 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.4667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 255.5 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.6 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138 | 69 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.5833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 184.6167 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 194.25 | 105 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.9 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201.5 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.7 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.4 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 219.8 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 221.4333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 252 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.8667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 748 | 68 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 824.3333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1525.7667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2420.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 14387.9166 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 41410.5 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 45055.3833 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 101.3064 | 379.9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.2333 | 29 | 1 | 1 | 1450-Other air supply problems | D3-Forced - Postponed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.942 | 64.38 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.76 | 62.4 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 268.25 | 64.38 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 566.8 | 62.4 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.2 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 156 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.8333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244.3 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.9333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 369 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 511.2 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.74 | 4.74 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.35 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.2 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.5667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.2333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.05 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.7333 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.1 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.3667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 247.1 | 14 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 248.9667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325.2666 | 68 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 456 | 48 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 505.4666 | 68 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 783.9 | 78 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 899.2667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.15 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1059.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6183.9167 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 39.0833 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 61.2667 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 964.1666 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21712.3183 | 9.7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 582.6667 | 38 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183.25 | 15 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.3333 | 55 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.8 | 24 | 1 | 1 | 1450-Other air supply problems | D3-Forced - Postponed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 502.1498 | 249 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.9167 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.1667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 341.1 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 577.0333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 597.15 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1277.6 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5708.6666 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.8 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125.1 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.1667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.4 | 48 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.9167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199.0333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210.8333 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.7667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.1 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2484 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1122.3333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 333.6667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1643.1667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6625.1833 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10100.55 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.9283 | 16.1 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.15 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.8333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 211.8667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.4667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 911.7167 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.6 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.35 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153.0667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215 | 43 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.5833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.8667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.05 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.3333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.25 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 197.8333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 477.6667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 114 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1579.6 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 87 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 150.65 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8576.75 | 91 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 33859.1666 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 906 | 151 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2137.8161 | 817 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.25 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.25 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.2333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.2 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 156.3 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.55 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.95 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.5 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.2667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 237.5333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.55 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.4333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.7833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.4833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301 | 43 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 479.8 | 12 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 699.8333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1744.3833 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 369.8333 | 70 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2610 | 58 | 1 | 1 | 1450-Other air supply problems | D3-Forced - Postponed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 263.12 | 62.4 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.3333 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.2 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6267 | 9.4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147.15 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.95 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.6667 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.9167 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.2833 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244.7667 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 275.1 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1341.5 | 26.83 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.2 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.5667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.3 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.85 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 232.05 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 254.3333 | 14 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.5 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330 | 120 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 336 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 646.75 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 939.4667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1690.2666 | 28 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.85 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413.3333 | 160 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24144.25 | 19 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 65 | 25 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 144.6665 | 280 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 18889 | 30 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.103 | 64.38 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2088.5998 | 531 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 452.6832 | 173 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 41.1667 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 195 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 211.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 270.8332 | 325 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 347.75 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1469.1664 | 430 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 164.5831 | 395 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 52.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13171.6665 | 350 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 416.5 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 444.5 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 850-Combined Cycle Block
1451 | Fluidized Air Fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 32710.1666 | 32.5 | 1 | 1 | 1451-Fluidized Air Fan | U1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.65 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 311.6666 | 170 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2413 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17140.5906 | 57.32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38166.7 | 314 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.25 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 188.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 448 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 720.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 733.15 | 341 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1027.5833 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2164.1666 | 98 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4259.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11825 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14172.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64103.6 | 136 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 135 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 224.5833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 312.9 | 149 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 485 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 812.3933 | 482.61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 940.4833 | 77.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 254.56 | 15.91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 325.81 | 10.51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.2 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.2667 | 2 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.75 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 499 | 60 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37149.1666 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 966 | 12 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13093.5 | 609 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11648 | 112 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27593.5 | 638 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 749 | 107 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 585.9165 | 395 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 8066.905 | 63.77 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 522.8665 | 253 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1391.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2026.6664 | 400 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2094 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4864.5 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8434.0665 | 217 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.55 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.2666 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.3333 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 244.8 | 96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 252 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364.9998 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 620 | 10 | 2 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 840 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10422 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28997.665 | 98.94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.8 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 105 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 791.6667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1235.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11670.4 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27495 | 117 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 125.55 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 130.22 | 7.66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 316.72 | 8.56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 388.68 | 9.48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 431.768 | 7.44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 14.3767 | 4.54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 140.94 | 7.83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 277.02 | 5.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.7 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 486 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7514.6666 | 160 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12790.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21843.5 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1614.8 | 24 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177200.8331 | 550 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4312.7 | 427 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 829.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1122.5167 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1798.6665 | 380 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6557 | 79 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 272 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 329.2333 | 238 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 579.6 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 636 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 640 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 800 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1790 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2680 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6793.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14783.2667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15751.19 | 49.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 105 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.3 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.55 | 101 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 206.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 445.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 734 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2897.6999 | 117 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3952 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4839.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7396.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 185 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17688 | 90 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.5 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 112 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 271.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33479.25 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 758734.9 | 147.7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132 | 110 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6384 | 798 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20.7 | 27 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21.15 | 27 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17785.1499 | 201 | 1 | 1 | 1455-Induced draft fans | U3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.25 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 132.5 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.9999 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320.6666 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 700 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 950 | 475 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1503.7499 | 225 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1725.5 | 170 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.5 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156 | 156 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.3333 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 206.8 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1132 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1800 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2138.4 | 59.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4085.9999 | 270 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18975.9516 | 90.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.35 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 475 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 736.6666 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3100 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 2182.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 567.796 | 14.46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 17.6 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.5 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.4167 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10515 | 12 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45494.1664 | 770 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1042.5 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1087.2667 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2078.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3750 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7333.2 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.4 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.2667 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.4 | 2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 207 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 434 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 519.7499 | 405 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 890 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2157.4 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3480 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8380.1 | 141 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19680 | 300 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109814.9166 | 155 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 920 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2575 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 254040 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84990.7695 | 133.77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 202.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.5 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 240 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12075 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.5 | 215 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1208 | 151 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12058.2 | 638 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 616.4433 | 63.77 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.11667 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1447.8332 | 170 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3950.1 | 231 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8677.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67888.4 | 344 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 138.6666 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.8833 | 169 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.5 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 351 | 9 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 415.3332 | 280 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 960 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1008 | 6 | 2 | 3 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1245 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1387.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9642.4999 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4259.1667 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5297.1819 | 265.08 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 240.3916 | 158.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2542.778 | 250.52 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 299 | 598 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2779 | 15.88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 568.3333 | 55 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 165.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.3333 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3601.2499 | 75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7502 | 12 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45819.2 | 96 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 302.1 | 106 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 565.3333 | 80 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1311.6666 | 100 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 559.1666 | 275 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18696.6665 | 395 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.2499 | 225 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 575 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 609.5 | 265 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1044.0399 | 91.05 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1805 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2713.333 | 440 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11821.5 | 111 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29119.3832 | 319 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.5 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129 | 3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 174.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.0666 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 410 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 686 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 869.094 | 327.96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1222.75 | 365 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2327.4166 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7327.4167 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7534.4383 | 74.66 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 331.2 | 138 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 916.85 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1533.3332 | 230 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3990 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5492.2667 | 38 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 209.2665 | 313.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 20745.6665 | 238 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1239.5075 | 180.95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 150.45 | 8.85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1476.902 | 6.51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 495 | 165 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12100.5555 | 178.87 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 444 | 296 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5376 | 112 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15223.9996 | 1320 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9697.5 | 431 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 847.2 | 48 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 141.3333 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390.8331 | 350 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642.96 | 45.6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 672 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1657.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2323.1667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2483.3333 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3690.5 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.9999 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.2665 | 208 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 264 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 460 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 492 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 603 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 894.3998 | 258 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2497.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2568.5499 | 141 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.5833 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.75 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 378 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.2 | 20.6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495.8333 | 250 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9051.0833 | 85 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 0.23333 | 2 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1841.6666 | 130 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5035 | 265 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43678.9166 | 65 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1133.3332 | 340 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27705.3 | 553 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13252.25 | 395 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 411.9996 | 618 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 2226.8 | 293 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 650 | Fluidized Bed | TRE | Winter | 534.24 | 143.1 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 12058.65 | 189.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 76.5 | 15.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 220.0833 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 549.0333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 812.25 | 171 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 75.15 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 110.9331 | 416 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 5960.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 138.6665 | 416 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 266 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 275.5 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 9.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 717 | 45 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 175.6 | 439 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1414.35 | 449 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.15 | 18.3 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3318.0833 | 145 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3688.5332 | 152 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4651.5 | 105 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2168.1329 | 644 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 421.6667 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4127.6666 | 140 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4956 | 60 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 11481.3333 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 16 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2940 | 140 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.2 | 18 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1040 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.8 | 244 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 397.5 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20058.5 | 770 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 146.85 | 99 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1426.45 | 607 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6923.75 | 145 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 40 | 12 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14356.7769 | 190.83 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 373.17 | 177.7 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 259.1333 | 92 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15588 | 30 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.6633 | 46.1 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 32 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2715.8282 | 264.1 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204 | 72 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7250.8328 | 770 | 1 | 1 | 1456-Induced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3642.5 | 30 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5337 | 60 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5904 | 48 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 750 | 120 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.75 | 55 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1437.75 | 405 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 805.5 | 30 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 845.5 | 190 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 80 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1743.8665 | 319 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2229.7066 | 68.96 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2534.1331 | 344 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.58333 | 5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 676.4 | 8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 473 | 43 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10580 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 712.8 | 324 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1206.9997 | 510 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1566.6664 | 400 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8702.4 | 444 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17134.32 | 437.1 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 1127 | 105 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 650-Fluidized Bed
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 218.6666 | 80 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 58.9 | 58.9 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 233.9998 | 270 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 309.6 | 72 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.9999 | 180 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1833.5 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2023.5 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.75 | 135 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1192.1498 | 339 | 1 | 1 | 1457-Induced draft fan lubrication systems | SF-Startup Failure | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12903 | 690 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 391.5 | 270 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 881.7333 | 34 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2622 | 570 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 262.8333 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1779.6665 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76.6666 | 200 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 208 | 120 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35786 | 580 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 62.5166 | 121 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74 | 74 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 160.9999 | 210 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 268.6666 | 260 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2683.3332 | 280 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1122 | 330 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2673.25 | 185 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 614.3333 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64305.3333 | 136 | 1 | 1 | 1457-Induced draft fan lubrication systems | D3-Forced - Postponed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33872 | 580 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.2667 | 29 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4393.6666 | 245 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7731.2497 | 375 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 456.6666 | 200 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42816.6666 | 350 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.2998 | 234 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8402.1998 | 516 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 457.8331 | 410 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4439.1665 | 350 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1044 | 145 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 823.145 | 85.3 | 1 | 1 | 1457-Induced draft fan lubrication systems | D3-Forced - Postponed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13070.3331 | 565 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 255.75 | 31 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1064.25 | 165 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12631.8333 | 190 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2411.5832 | 215 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 162.9 | 181 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1166.6665 | 250 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.8832 | 227 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18904.1665 | 650 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1393.5666 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 427.5 | 95 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2119.9 | 102 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1746 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8404.1666 | 125 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6939.9999 | 150 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1611.8166 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1735.5 | 117 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1441.2999 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2237.3333 | 160 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1498.65 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1471.1666 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21708.4999 | 330 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1936.7666 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1198.5 | 102 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1202.8 | 97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1503.65 | 87 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1146.3333 | 190 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 116.375 | 9.5 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 981.3333 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 277.6666 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307.0833 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2114.2333 | 34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.5255 | 39.63 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6984 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 389.6665 | 208.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.82 | 5.97 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.8133 | 2.93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.33 | 1.88 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.2 | 12.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.0667 | 4.6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 87.6573 | 22.67 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 140.28 | 11.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 291.428 | 17.77 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 326.6723 | 14.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 457.776 | 26.01 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 465.3 | 33 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3753 | 135 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 30271.25 | 75 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3329.9333 | 199 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53480.4 | 328 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4296.3998 | 552 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4716.25 | 245 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 33 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 90 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.4 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 530.4166 | 95 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26683.2 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96040.12 | 396.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 199.5 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2120.9783 | 29.39 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33843.3333 | 130 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.1095 | 16.23 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 232.6267 | 11.68 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6345.1785 | 275.08 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.1837 | 3.26 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.502 | 18.84 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 86.319 | 8.34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.9643 | 3.34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.3433 | 6.26 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.7667 | 11.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119.6763 | 28.27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 224.9667 | 31.76 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 311.1717 | 30.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 138.138 | 17.71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 3847.1 | 31 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4494.8332 | 298 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4490.7498 | 345 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2180 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 78.6666 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 236.25 | 175 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11220 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.6203 | 19.07 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.0666 | 137 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 234.3333 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 551.4 | 36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1179.2 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1330 | 120 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2287.8 | 123 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2438.9166 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34967.2167 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41040 | 57 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45180 | 240 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2688 | 36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4828.4333 | 82 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.6 | 3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.07 | 13.01 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 276.76 | 18.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 667.696 | 27.84 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.8802 | 15.11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.6375 | 8.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60.0767 | 13.45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.1355 | 5.07 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 66.8308 | 4.03 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 141.31 | 10.87 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 62.662 | 19.38 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 67.66 | 7.96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.7653 | 30.28 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.1167 | 8.78 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 190.736 | 51.09 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 516.48 | 21.52 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 280.8 | 7.02 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14469.9 | 417 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 223.8331 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 9405 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 365.75 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1510.8331 | 350 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1957.0833 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38771.2 | 128 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42408 | 57 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.28 | 32.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11275.9999 | 240 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 316.6666 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1047.0833 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1250.85 | 269 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.665 | 3.15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.76 | 4.47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.1433 | 24.04 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181260 | 251.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.402 | 1.94 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.774 | 3.21 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8202 | 12.61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.865 | 8.3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.795 | 3.45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.022 | 4.98 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.4717 | 3.85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 377.303 | 18.42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.1213 | 3.92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11.2255 | 4.71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.595 | 17.73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.0977 | 8.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 208.74 | 9.94 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 496.243 | 21.67 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 684 | 28.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 668.15 | 19.09 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.3333 | 10 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20.25 | 5 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1846.9166 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.3416 | 76.1 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9389.3664 | 662 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 250 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1683 | 5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3711.6666 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13925.8 | 196 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.5 | 130 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 182.75 | 215 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 242.8225 | 9.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1229.1666 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56610.765 | 130.59 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 555.05 | 6.53 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 565.4166 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21823.2 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 0.7 | 2.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 50.9833 | 13.3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.96 | 3.45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.82 | 9.04 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16 | 16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.7417 | 5.15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.03 | 8.22 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.0983 | 9.98 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110.6453 | 9.02 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 212.4395 | 19.11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 293.25 | 12.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4.9163 | 3.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13.7573 | 4.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.2358 | 5.59 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 32470 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 671.6666 | 31 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 163.2 | 10.88 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3592.0832 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5361.4166 | 245 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5568 | 116 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220 | 110 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3645.2998 | 261 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43949.25 | 85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 138726.1332 | 176 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.6666 | 137 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.9999 | 180 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 302.4525 | 24.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 695.4666 | 128 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32711.2167 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 558.5998 | 252 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2166.7775 | 43.35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6933.6075 | 61.55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11234.1666 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21392 | 764 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 26220 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.0423 | 8.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 363.8272 | 15.17 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 579.8448 | 39.49 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.806 | 2.67 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.2313 | 18.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.876 | 4.68 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.8 | 6.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.0217 | 19.78 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.72 | 7.68 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.1647 | 6.62 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.0733 | 9.46 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 169.344 | 17.92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 182.3113 | 28.12 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 357.5583 | 20.05 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 394.1693 | 29.27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 495.7167 | 24.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 636.2778 | 26.53 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 21635.2032 | 169.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 62563.4332 | 146 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1445.9333 | 82 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 912.6666 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51122.9333 | 208 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 915.6666 | 335 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5103.3332 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 364.25 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 8570.25 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.6667 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2694 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9970 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70506.3333 | 220 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 104.8332 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50155.9999 | 240 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.3333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 296.25 | 15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3542.2333 | 94 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.328 | 6.24 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.48 | 5.64 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.6193 | 7.87 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.652 | 14.48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.8 | 14.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105.9025 | 38.51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 162.8347 | 9.08 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 167.5167 | 23 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 171.7435 | 11.67 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.0427 | 11.98 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 332.794 | 21.61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 364.56 | 17.36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 445.28 | 19.36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 808.4782 | 33.71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 1408.2 | 18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 146.34 | 8.13 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 805 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 39464.1666 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1306.6666 | 245 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10800 | 225 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 800 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1970.4 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | U2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7366.25 | 355 | 1 | 1 | 1470-Induced draft fan motors and drives | U2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129 | 129 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.3333 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 489.1667 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1311.8 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16126.6666 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.6832 | 137 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.9166 | 137 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1467.5 | 30 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2671 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3856 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1845 | 82 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5340.6 | 86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16842.4 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.94 | 5.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.226 | 8.76 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280.4666 | 150.25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.1433 | 4.22 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.49 | 4.77 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25 | 12.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.3 | 5.93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 428.0033 | 23.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 617.9066 | 76.6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60379.7332 | 212.48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 314.3 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1380 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76006.3333 | 220 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 607.4166 | 197 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22795.4998 | 630 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21909.3331 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 4668.3333 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 196.6667 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 620 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 864 | 27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 64.5 | 43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 509.1667 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11.4 | 19 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3.8333 | 23 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 7.1666 | 43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 588.3333 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2653 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 13921.6 | 70.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 17.25 | 69 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 31.4999 | 189 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2025.1665 | 419 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 209.6666 | 34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13.8833 | 119 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 479.7 | 234 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 257.84 | 26.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 855.3996 | 546 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27506.6666 | 160 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300 | 100 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1704.25 | 15 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5550.5332 | 266 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7355.8333 | 10 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6555.3333 | 20 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 509.1666 | 130 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 662.5 | 265 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.6 | 158 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1050.8333 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1268.5 | 10 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.6 | 96 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 260.6666 | 230 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1213.3332 | 260 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 208.8 | 261 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.1333 | 71 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.9167 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 408.8 | 146 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 603.3333 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1323.2066 | 193.64 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1456 | 13 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1615.25 | 105 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3918.75 | 285 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1628.7665 | 262 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D3-Forced - Postponed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1150.25 | 535 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42855.25 | 565 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1664.8832 | 523 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 148.7343 | 217.66 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1039.1036 | 163.21 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3362.6666 | 260 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5581.3332 | 260 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.6 | 46 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235.5 | 10 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 351.1666 | 245 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5242.5 | 90 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 815.9998 | 306 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17643.9998 | 330 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116.6667 | 35 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 295.55 | 69 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.6667 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1035.8333 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1049.9999 | 180 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1360.4166 | 25 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2050.25 | 295 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 233.8333 | 115 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8872.05 | 627 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 379.5 | 110 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1439.1666 | 110 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2436.6 | 393 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.2533 | 26.72 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1308 | 240 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5238.75 | 275 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6364.4165 | 265 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45543 | 282 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 420 | 56 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22.5 | 30 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7280 | 130 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 488.7166 | 71 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1990.25 | 95 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2248 | 281 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 19.1667 | 23 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 17653.2 | 626 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2660.2666 | 344 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 526.9333 | 104 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1932.4966 | 69.1 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1551 | 60 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 898.7 | 66 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 67.3666 | 86 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 84403.9166 | 55 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1861 | 60 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5903.9998 | 540 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4050.7998 | 228 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97449.0666 | 89 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 191.3332 | 140 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2201.3333 | 130 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 46224.1666 | 50 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 9094.5 | 129 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 558.75 | 149 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 92.4 | 21 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120.75 | 105 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 318.2 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 649.2832 | 239 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1292.8 | 101 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12887.0833 | 157 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.2166 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 121.9 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 17.55 | 27 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1372.7999 | 198 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 516.8 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.8333 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 105.2333 | 77 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282.03 | 40.29 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 524.3333 | 121 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.3333 | 28 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 241.2167 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2968.95 | 197.93 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3153.3665 | 247 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.4832 | 289 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9356.55 | 469 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3167 | 5.18 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43.45 | 33 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3429.9997 | 420 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.98 | 27.49 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 121.2666 | 68 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 150.8 | 87 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 171.1667 | 26 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6 | 30 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.6667 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 565.75 | 73 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 570.4166 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 896.7999 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2511.6833 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5205.9999 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.3333 | 4 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.1333 | 28 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 62.7 | 20.9 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 773.4499 | 93 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19 | 60 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 137.9498 | 267 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 147.7667 | 22 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 627.8999 | 117 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 939.5 | 30 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.7 | 6 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 515 | 103 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2977.3332 | 176 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3978.3332 | 155 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1893.0663 | 496 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 54.5 | 30 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.3 | 42 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.8333 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 433.1833 | 47 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 632.7 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1145.65 | 33 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 19789.9333 | 28 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49.8833 | 41 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.8 | 38 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 242.8333 | 31 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2029.5 | 198 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3774.1999 | 339 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96.8 | 121 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1578.9 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4440 | 555 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.7 | 6 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 230 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 542 | 542 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 561.1 | 62 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 644 | 140 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4 | 24 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22 | 22 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.5 | 47 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95.5667 | 47 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.8332 | 283 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 665 | 475 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 425.483 | 521 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 870.2 | 76 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1452.8666 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2255 | 220 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3588 | 260 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.82 | 6.91 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185 | 185 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209.01 | 69.67 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 282.5333 | 26 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436 | 109 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1202.04 | 85.86 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4946.3333 | 110 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.7667 | 29 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.9999 | 120 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 82.6333 | 74 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 611 | 130 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 613.5833 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 780.3666 | 82 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 278.8333 | 35 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8370.8665 | 614 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1170 | 200 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 310.8 | 77.7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 231.5583 | 75.1 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.7332 | 143 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.55 | 37 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.8332 | 310 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382.4332 | 149 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 260 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 533.3433 | 74.42 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.7332 | 203 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.6 | 168 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 336 | 160 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3658 | 118 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 10 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.8999 | 87 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.7833 | 113 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275 | 220 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630 | 108 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1497.6332 | 502 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 178.6 | 47 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.95 | 87 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62911.9999 | 120 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3832.3999 | 156 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133 | 133 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3747.3332 | 140 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35196.2333 | 133 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 144 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390.8331 | 335 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1141.6166 | 143 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11786.6666 | 100 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 486 | 81 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.5367 | 13.64 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 890.5 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1103.6 | 248 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3122.4999 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85068.9 | 378 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 76.5 | 170 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 296.6666 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1366.6666 | 125 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2514.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 239.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 475.2 | 22 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2444 | 94 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1214.1832 | 277 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1171.2499 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 169.9999 | 120 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 475.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24689.0663 | 568 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 257.92 | 62.4 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.6 | 272 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 227.9218 | 192.61 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 565.8333 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1515 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3399.5 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4173 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 191.4 | 99 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 624.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 645.2498 | 267 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1050.1832 | 481 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1176 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 284.25 | 45 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 333.7666 | 31 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 460 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 295.5 | 9 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 484.0333 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 353.8498 | 303.3 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.4 | 148 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.8333 | 79 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 485.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 847.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2310 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.75 | 21 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 268.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 359.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 488.5832 | 143 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 603.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 983.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22525.4665 | 241 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.5 | 97 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.6 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.1 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 248.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 393.75 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 472.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5227.7499 | 165 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 795.9 | 379 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51042.1332 | 448 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5315.2494 | 855 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 315.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37072.9999 | 393 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67180.9665 | 229 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.1985 | 32.37 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474 | 24 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1636.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6425 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.3332 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 225 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27034.3331 | 730 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6691.4832 | 209 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 199.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 278.85 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2068.633 | 458 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.6 | 103 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 622.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.3333 | 1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.7 | 9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1554 | 185 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3574.2498 | 255 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5820.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 190.3999 | 84 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 616.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1512 | 112 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 563.2665 | 238 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 480 | 80 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 175.972 | 64.38 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2916.4165 | 395 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21291 | 151 | 1 | 1 | 1480-Other induced draft fan problems | U2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.6332 | 191 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 465.8333 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.55 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 371.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 385.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 763.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1418.0833 | 17 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3088 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49062.75 | 55 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 15.6 | 4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 615 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1999.9999 | 120 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4900.8666 | 164 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 241.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 342.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3243.6 | 318 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2297.0996 | 558 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4754.9997 | 900 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2951.6665 | 575 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.6667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.25 | 17 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 191.3332 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 331.5 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1925 | 175 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2262 | 87 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4771.4999 | 90 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8470.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55991.9 | 274 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69526.1 | 343 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 279527.7997 | 393 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.8666 | 163.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 183.15 | 111 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 213.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 512.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5258.1 | 51.55 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.4333 | 24.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 132.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1181.0667 | 34.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 116.64 | 12.96 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 208.8 | 24 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 328.6666 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 366.3333 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 492.1 | 14 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 576 | 16 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4982 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 449.5 | 58 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 431.1666 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2531.4998 | 249 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 629.235 | 53.1 | 1 | 1 | 1480-Other induced draft fan problems | U3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.3333 | 73 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.9 | 58 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 155.3332 | 233 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.6666 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 351.6665 | 211 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1311.2666 | 221 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17595 | 34 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90855 | 90 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.4 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 71.25 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.6 | 38.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3607.5 | 195 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 106080 | 85 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.6666 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 567.3333 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.5 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 285.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 410.8333 | 17 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 619.6666 | 260 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11342 | 107 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 97.5 | 32.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 15840 | 330 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2210 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 213 | 21.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 37.99 | 13.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 870 | 174 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11907.4999 | 330 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2881.3333 | 80 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3260 | 80 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3697.3997 | 417 | 1 | 1 | 1487-Air heater (tubular) | U2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 3 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2338.6666 | 80 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208.9998 | 228 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.8333 | 25.9 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1866.6664 | 400 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7791 | 53 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20553.8666 | 77 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.0666 | 288.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.6666 | 248 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1030.8999 | 183 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3933.4833 | 61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.6 | 36 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 267.75 | 315 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.3 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 391.0833 | 95 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.4 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30.3333 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6902.1333 | 104 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12756.3328 | 770 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 212250 | 750 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24412.1664 | 355 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.9332 | 128 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 822.25 | 253 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1264.9999 | 330 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1418.85 | 27 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2915.3165 | 211 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25872 | 330 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49111.5 | 290 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18472.6665 | 458 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 96920.9164 | 355 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 99280.9999 | 210 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2295.4666 | 64 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7722 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23823.3332 | 280 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.5999 | 258 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 240 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202 | 101 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 627.0833 | 175 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1840 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2826.6666 | 320 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245.8332 | 250 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 424.2666 | 148 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1727.7166 | 251 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10052.64 | 23.27 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3578.8 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.3 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.7667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.9 | 29 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.05 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11260.6666 | 140 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13871.6665 | 410 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30097.8 | 654.3 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 639.8 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1284 | 428 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1410 | 200 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7392.6932 | 17.53 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7575 | 300 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35739 | 228 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 175 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 562.8 | 63 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1397.2 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48.75 | 45 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4015 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10536.96 | 27.44 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 304 | 304 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1416 | 5.9 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.1667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.3167 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22130.5332 | 158 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.1833 | 41 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1530.7999 | 258 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8058.1999 | 258 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18314.3331 | 658 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6672.4998 | 255 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72090.7494 | 855 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6617.9999 | 360 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285.25 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 513.5 | 158 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1201.6665 | 350 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2653.2 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5257.6333 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16866.6666 | 115 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.5 | 323 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8081.23 | 11.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.0666 | 88 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1211.845 | 457.3 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 74.6666 | 320 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3312.8 | 10.1 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.25 | 75 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6409 | 290 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 767.968 | 16.48 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5000 | 500 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5346 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7254.247 | 20.02 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 825.6333 | 94 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2082.5 | 350 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1484.9 | 31 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7693.2 | 21.37 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.8667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 248.6 | 132 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1.1666 | 70 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.6833 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16489.9998 | 600 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 64965 | 355 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 53344.1831 | 353 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104148.7166 | 311 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.2 | 36 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 505.2666 | 212 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4232.9 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8886.6664 | 430 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1024 | 48 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1118.5666 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2327.0567 | 11.02 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3525 | 94 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3735.1999 | 84 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4610.2 | 84 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11742.5 | 305 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20251.25 | 51 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.4999 | 159 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2273.75 | 535 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 907.7 | 313 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.8667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.8166 | 31 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.4 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.25 | 25 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44402.9166 | 305 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27555.8998 | 558 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 224.2158 | 22.61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 574 | 328 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 711.6662 | 700 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3773.3833 | 211 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 295.2 | 108 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1545.8331 | 350 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3697.2498 | 345 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11876.3332 | 158 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47124 | 308 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.4999 | 198 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 27 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16477.44 | 24.52 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1058.9999 | 180 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1173.3333 | 80 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.8167 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.8333 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2280 | 144 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31468.6158 | 1243 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40517 | 620 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 10826.125 | 642.5 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13032.2498 | 231 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 200.25 | 5 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 511.9999 | 240 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1074.2087 | 8.14 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D2-Forced - Delayed | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14427 | 90 | 1 | 2 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61290 | 270 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7400 | 370 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449 | 6 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1054.9 | 22 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 479.7833 | 11 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 880.9 | 6 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1696.3167 | 17 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.65 | 21 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 487.6667 | 11 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 64292.6667 | 14 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2584 | 16 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 26306 | 21 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 40188.6333 | 14 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14320.9 | 277 | 1 | 1 | 1492-Air heater fouling (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1910.8 | 34 | 1 | 1 | 1492-Air heater fouling (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 215.3616 | 69.1 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.5333 | 16 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2512.9 | 26 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 738.9333 | 16 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1174.5 | 6 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 884.8 | 16 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3864.3 | 6 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 468.75 | 37.5 | 1 | 1 | 1492-Air heater fouling (tubular) | U1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.5833 | 43 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.8667 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1188 | 33 | 1 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2152.3333 | 44 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2849.4666 | 43 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.3999 | 80.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 549.6166 | 49 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9439.2 | 48 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 722.5 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8451.6666 | 110 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2366.7 | 14.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3286.6666 | 200 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38599.9998 | 300 | 1 | 1 | 1493-Air heater fouling (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1991.5 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14542.6667 | 13 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78397.6 | 34.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.6667 | 50 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.6 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 252.2333 | 47 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 502.25 | 49 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1854.9333 | 64 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19977.5 | 75 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 181.3333 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 203.4333 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2955 | 50 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2010 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2305.5 | 8.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4961.7 | 11.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1332 | 24 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3366 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7604 | 38.02 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10594.65 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 294.8167 | 18.05 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1295.55 | 27 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2524.88 | 25.59 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3939.8 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41150 | 100 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6.375 | 22.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11058.5832 | 131 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.8333 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.6 | 10.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.6667 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2265.4 | 9.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32253.6497 | 507 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.9972 | 22.37 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 230.3 | 7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1509.75 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1393.76 | 74.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4700 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16180.0333 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 936.0999 | 222 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7196.6666 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5093.2 | 10.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1317.6666 | 59 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1822.8 | 24.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5531.8 | 51 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 923.6666 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4320.8333 | 61 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12064.5 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15730.98 | 65.82 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5030 | 150 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 896.2067 | 10.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 693.5 | 9.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2384.25 | 51 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7364.1 | 18 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.7333 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.5 | 29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5921.3 | 42 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16990.9333 | 54.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 0.91666 | 27.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.8333 | 130 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 342.18 | 19.01 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 601.4 | 9.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 616 | 7.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.25 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720.5 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 792 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1426.6666 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2450.25 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2521.2 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16060 | 50 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1604.2666 | 64 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1751.12 | 31.27 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2599.5 | 9 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6698.5666 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.4 | 5.2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345.6 | 4.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4800 | 200 | 1 | 1 | 1493-Air heater fouling (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17400 | 300 | 2 | 2 | 1493-Air heater fouling (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.54998 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1294.8333 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.5333 | 49 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.725 | 6.18 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58 | 29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 455.4 | 44 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 529.0333 | 59 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1791.7 | 69 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6138 | 59.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46886.64 | 69.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2294.25 | 105 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10700.04 | 68.59 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395.1733 | 5.6 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164 | 16.4 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 453.2 | 10.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 688 | 8.6 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38400 | 300 | 1 | 1 | 1493-Air heater fouling (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42300 | 300 | 2 | 2 | 1493-Air heater fouling (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179.6667 | 35 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 722.5 | 30 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 3040 | 190 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | SF-Startup Failure | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2937.6667 | 10 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.1 | 6 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84 | 15 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229 | 30 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304.3333 | 20 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2633 | 15 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 371.6667 | 25 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.4167 | 23 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8990.6665 | 440 | 1 | 1 | 1500-Air heater soot blowers | U1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 25 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.25 | 25 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360 | 240 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.3777 | 155.57 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 502.2 | 186 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.8833 | 79 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 157.025 | 28.55 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4870.8333 | 70 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 327.5 | 150 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 435 | 45 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235833.6329 | 578 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61952 | 352 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | SF-Startup Failure | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69.1333 | 122 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1726.2583 | 146.5 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380.5165 | 289 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39 | 90 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2457.25 | 15 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.3333 | 13 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 579.9833 | 89 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70274.5833 | 115 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 353.2666 | 28 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 893.75 | 55 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435.596 | 155.57 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 206837.5833 | 85 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 16974.9999 | 150 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1948.3333 | 100 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175560 | 770 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9165 | 390 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10249.2 | 78 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63128.4498 | 627 | 1 | 1 | 1512-Flue gas expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15196.8 | 192 | 1 | 1 | 1512-Flue gas expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25252.3332 | 388 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 657.3332 | 340 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Off-Peak | 2832.1999 | 102 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1522.2 | 59 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28383.9331 | 622 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | SF-Startup Failure | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8295.8332 | 275 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U3-Forced - Postponed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52906.0829 | 635 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U3-Forced - Postponed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96 | 20 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6480 | 270 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9459.9991 | 1320 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.575 | 1.5 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 777.1 | 38 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 88 | 60 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 504 | 135 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.4 | 8.4 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.1 | 12.7 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 639.4 | 4.6 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.5 | 10 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.7 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.8333 | 65 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2325.3 | 138 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 713.4 | 8.2 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1021 | 60 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3114.3 | 10.5 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21623.3329 | 650 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.8666 | 74 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265 | 50 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1519.4333 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7938.2 | 57 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2487.24 | 10.8 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.8666 | 42.88 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469.6667 | 10 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 24199.8332 | 535 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11904 | 16 | 1 | 2 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 864 | 8 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2479 | 13.4 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5022 | 10.8 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 381.5333 | 118 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 20326.4833 | 59 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 984.8666 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2233.5666 | 74 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16029.1 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 8.5 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 380 | 9.5 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 662.5067 | 6.4 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2150.2 | 12 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 233.05 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 876.9 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1049.3833 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5233.75 | 79 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336.7 | 3.7 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589 | 6.2 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3062.4 | 11.6 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6153.085 | 12.9 | 1 | 1 | 1530-Other flue gas problems | D2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 369.8 | 43 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 223.1667 | 10 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 4939.6667 | 29 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1512.2833 | 31 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1016.6666 | 200 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 680.9 | 619 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5315.0496 | 663 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 100.2664 | 376 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 326.3333 | 89 | 1 | 1 | 1535-Flue gas recirculating fan | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1536 | Flue gas recirculating fan dampers | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67737.8999 | 387 | 1 | 1 | 1536-Flue gas recirculating fan dampers | U2-Forced - Delayed | 100-Fossil-Steam
1536 | Flue gas recirculating fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2949.9165 | 455 | 1 | 1 | 1536-Flue gas recirculating fan dampers | SF-Startup Failure | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 216.4666 | 191 | 1 | 1 | 1550-Flue gas recirculation fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1555 | Flue gas recirculation fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1433.4998 | 705 | 1 | 1 | 1555-Flue gas recirculation fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1560 | Other flue gas recirculation fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 798.5297 | 509.7 | 1 | 1 | 1560-Other flue gas recirculation fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1560 | Other flue gas recirculation fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1014.3332 | 358 | 1 | 1 | 1560-Other flue gas recirculation fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1560 | Other flue gas recirculation fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2093.75 | 312.5 | 1 | 1 | 1560-Other flue gas recirculation fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69208.4883 | 736.13 | 1 | 1 | 1570-Flue gas recirculation ducts | U1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.5 | 21 | 1 | 1 | 1570-Flue gas recirculation ducts | D1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 656190.5 | 658 | 1 | 1 | 1570-Flue gas recirculation ducts | U1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 17950.8329 | 650 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2422.4999 | 450 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 87375 | 750 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3331.8 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8640 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8652 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 8928 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 26 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1730.6 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8928 | 12 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3079.9999 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2047.5 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63426 | 330 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36424 | 60 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 681.9998 | 330 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1455.9999 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1020 | 60 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D3-Forced - Postponed | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14340 | 60 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1680 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12622.5 | 330 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53886 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23712.4999 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.9999 | 180 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5280 | 330 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97524 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 60 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D3-Forced - Postponed | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1050 | 210 | 1 | 2 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D3-Forced - Postponed | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22676.4999 | 210 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11654.4998 | 330 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1648753.5 | 510 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | U1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 506.11 | 235.4 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 200.4164 | 325 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 560.9831 | 347 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1121 | 380 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 6009.1996 | 543 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4070.4 | 48 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 146.4666 | 169 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 205.8 | 126 | 1 | 1 | 1591-Stack damper and linkage | SF-Startup Failure | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 149.4499 | 147 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 119.8499 | 153 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 132.3833 | 169 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 125.0499 | 123 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 103.5533 | 63.4 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 852-CC steam units
1592 | Stack damper linkage motors | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 637 | 147 | 1 | 1 | 1592-Stack damper linkage motors | U1-Forced - Immediate | 851-CC GT units
1592 | Stack damper linkage motors | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 132.2999 | 162 | 1 | 1 | 1592-Stack damper linkage motors | U1-Forced - Immediate | 851-CC GT units
1592 | Stack damper linkage motors | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 146.9999 | 180 | 1 | 1 | 1592-Stack damper linkage motors | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675.8 | 62 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2670 | 120 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3038.7499 | 165 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 494.6667 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 6994.8 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6588 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 65880 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2664 | 80 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 2.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.94 | 2.77 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.5 | 1.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54 | 2.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.11 | 1.77 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.89 | 2.33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102 | 5.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122.14 | 3.94 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 6.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.11 | 9.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 591.6 | 10.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1030.7666 | 107 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2568.24 | 11.89 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.97 | 4.69 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.8 | 3.19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.42 | 5.02 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135.66 | 6.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 321.7902 | 8.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 334.8 | 3.72 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15477.4664 | 824 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 249.6 | 72 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.2 | 52 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 608 | 38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14680 | 120 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.8 | 2.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 757 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 2829 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 29.6 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 4.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.02 | 4.54 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.05 | 4.85 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.81 | 1.31 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.6 | 3.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.08 | 2.28 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.82 | 2.38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.9 | 3.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.23 | 2.73 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.5333 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274.715 | 4.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93 | 6.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118 | 5.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.98 | 7.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343.4 | 4.04 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 955.32 | 12.57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1596.87 | 48.39 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.36 | 5.28 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 4.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 18148.433 | 434 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | SF-Startup Failure | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 314.8933 | 171.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 565.5 | 435 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 417.8499 | 183 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.25 | 25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1520 | 80 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15367.5 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.35 | 27 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.5833 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.58333 | 0.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.75 | 0.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124.5833 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428.4 | 42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 505.4 | 42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 262.2 | 228 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.96 | 3.92 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.04 | 3.28 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 3.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.92 | 4.32 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306 | 6.12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.02 | 16.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153 | 4.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198 | 6.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 539.7 | 7.71 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1280.5 | 6.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.36 | 1.72 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.2 | 5.56 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.09 | 2.33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 211.14 | 6.21 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 840 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D3-Forced - Postponed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4524.45 | 651 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6261.15 | 469 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 64.8 | 64.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1171.6666 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 399.7 | 42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 838.9333 | 1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 16470 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 592.6666 | 70 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.15 | 1.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.98 | 2.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 2.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.9 | 4.65 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.53 | 6.51 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1070.85 | 32.45 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12520 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 426.16 | 76.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1019.2 | 728 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 196.8 | 164 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2374.1664 | 385 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4260 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.5 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 772.9333 | 187 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.96 | 6.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 382.08 | 5.97 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54 | 4.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.04 | 4.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.96 | 4.16 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 977.04 | 7.08 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.2 | 3.56 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1047.6 | 8.73 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.1783 | 76.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2222.9166 | 275 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 642.6 | 42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20230.8333 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.5 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 297.5417 | 2.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1624.9999 | 75 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.88 | 3.87 | 2 | 2 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.1 | 3.47 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179 | 8.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 208 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 462.84 | 5.32 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.88 | 8.06 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.04 | 3.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.6 | 3.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 249.09 | 4.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 353.5 | 7.07 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2287.35 | 5.85 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 277.6786 | 171.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.25 | 47 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1791.6666 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83.25 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2035.8 | 313.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.15 | 0.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.8333 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.86 | 2.38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 288 | 2.88 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 370.26 | 1.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.98 | 10.14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 4.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.07 | 4.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.99 | 2.07 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.18 | 3.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.56 | 4.73 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.41 | 4.57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78 | 3.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.23 | 1.13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.12 | 2.32 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.6 | 4.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.7333 | 16 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106.1667 | 14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6625 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20050.8333 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 518 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 943.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 88.9166 | 55 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 39528 | 12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 703.5 | 70 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.03 | 2.61 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.04 | 3.16 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.04 | 1.41 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.04 | 8.21 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.25 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 375.06 | 19.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 377.04 | 31.42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 529.125 | 8.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.02 | 4.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2539.7999 | 108 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 25713.333 | 560 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4500 | 100 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Winter | 146.2 | 102 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 120 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 150 | 15 | 1 | 3 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 180 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 930 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 960 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 774.4832 | 299.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 105 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 243.1 | 16.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 892.6333 | 61 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1305 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 6810 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 26.6399 | 199.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 345 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 204.0133 | 10.7 | 2 | 2 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 240.24 | 12.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17.6667 | 4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 56 | 20 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 89 | 20 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 334.2665 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 619.4665 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22596.75 | 747 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1164.2664 | 472 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 23.2 | 48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 301.8832 | 307 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1015.58 | 700.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 101.6666 | 61 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 405.5828 | 785 | 1 | 2 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1452.0999 | 78 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 785.3999 | 153 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 12637.4082 | 376.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 8409.9165 | 455 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4860.7999 | 186 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.6 | 258 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 16 | 48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4976.6498 | 723 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10640 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11231.1665 | 395 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2467.4999 | 450 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 219.9996 | 528 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 386.0999 | 81 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4350 | 500 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 119.9293 | 7.48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.2498 | 249 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 345.1 | 493 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 730.9998 | 645 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1016.4998 | 570 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9291.3328 | 770 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11211.4165 | 395 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1891.2831 | 559 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 374.4 | 144 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 379.4164 | 785 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5562.3447 | 495.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 218.1666 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1618.4 | 578 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4150 | 200 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 760.8 | 3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2053.3332 | 448 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2070.9998 | 570 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.0999 | 231 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112.1333 | 116 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 441.1 | 401 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7245 | 575 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 436.9996 | 570 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 817.8 | 564 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1823.5998 | 564 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4408 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6217.8 | 723 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10798.3331 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 374.5 | 107 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2897.4831 | 559 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 222.6997 | 393 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1264 | 320 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4135.95 | 707 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208277.7332 | 269 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4621.5 | 395 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7646.0329 | 700.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10031.6665 | 650 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6471.4 | 524 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 166.2666 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 19024.25 | 245 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 677.5998 | 528 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1848.6 | 234 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3621.5665 | 581 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 36612.333 | 455 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10961.0664 | 448 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5679.9164 | 749 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10426.6662 | 736 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 17342.6514 | 788.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 184.1833 | 43 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 684.9333 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3007.2498 | 345 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4832.7 | 89 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.6666 | 320 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15472 | 4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1057.5832 | 245 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2479 | 335 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1293.0998 | 579 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5290 | 575 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.6 | 48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15.7667 | 47.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 51.025 | 47.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 81.9 | 78 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 448.7332 | 254 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 30636.533 | 524 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.3332 | 200 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3000.4495 | 747 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1102.0829 | 575 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1200 | 300 | 2 | 2 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80642 | 661 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.7 | 342 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 243 | 162 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1386.9998 | 570 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3798.6665 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2697.2164 | 427 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.5416 | 47.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3182.8331 | 565 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 7 | 6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | WECC | Off-Peak | 3094.4666 | 266 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 273.3832 | 349 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 80.55 | 96.66 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 22.6666 | 40 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 106.4332 | 206 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 368.3272 | 649.99 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 494 | 260 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 7877.1 | 341 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 121.725 | 270.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 264 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 6747.0996 | 654 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 247.9673 | 270.51 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 104.6666 | 40 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 128 | 128 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | NPCC | Summer | 198.3333 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 712.4999 | 171 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 28.5167 | 29 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2.8332 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2531.9999 | 180 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 412.6482 | 149.15 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 59.5 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Winter | 807.1666 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 15345 | 155 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 158.321 | 186.26 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Winter | 84.15 | 187 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 21.6333 | 22 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 451.2499 | 285 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2022.2999 | 162 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 6724.9332 | 248 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 5980.4666 | 218 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 56.6666 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 79.2 | 176 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1537.0832 | 155 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 983.625 | 152.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 63.8573 | 10.19 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 1722.7 | 322 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1338.7499 | 135 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 248.9999 | 90 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 149.4666 | 236 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 117.1332 | 251 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 47.6666 | 143 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 253.7 | 59 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 124.6 | 178 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 967.5 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 13207.5 | 135 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 19.6667 | 20 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 66.8 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 41.8332 | 251 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2401.5997 | 474 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.6 | 18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28 | 30 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1331.55 | 11 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1521.6 | 72 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 37195.0166 | 103 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 767.05 | 667 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2471.4664 | 662 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 699.1996 | 552 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2167.4665 | 256 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 60.3333 | 20 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 983.5 | 562 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 352.8333 | 145 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9.69 | 11.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 552.5715 | 85.67 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 33055.5333 | 172 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 139.308 | 232.18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 320.25 | 105 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 523.4665 | 208 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1456.2166 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 459.9996 | 600 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10355.9496 | 627 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5172.75 | 855 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1052 | 526 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5067.5 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.1166 | 67 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.8 | 58 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 312.6666 | 56 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 626.7 | 18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 35660.1666 | 110 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2378.7497 | 825 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 844.9 | 102 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4995.6 | 552 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 869.9997 | 522 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.45 | 121 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.6 | 172 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.15 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192.0498 | 501 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 637.5 | 30 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1699.677 | 222.18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1796.1682 | 242.18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 614.7998 | 696 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5469.0996 | 546 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1775.7665 | 638 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6428.8 | 448 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5228.1666 | 254 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9928.6665 | 530 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.05 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 464.8 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 898.8447 | 175.67 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5680.5 | 105 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2459.8 | 502 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.69999 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.0666 | 28 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 262.4666 | 62 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 181.3332 | 128 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 662.4333 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1354.6666 | 254 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 101.75 | 185 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 145 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 4400 | 110 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 163.7163 | 517 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 617 | 617 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4514.9996 | 630 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5800.6664 | 770 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 91.9996 | 552 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 115.9666 | 98 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7979.9998 | 360 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 145.1666 | 134 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3079.9999 | 330 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 507.4998 | 609 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1168.4998 | 342 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 529.1666 | 254 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1139.6998 | 522 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.3 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.9333 | 68 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 97.5 | 18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9.55 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 502.25 | 105 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28503.2666 | 172 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 623.9 | 734 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4422 | 660 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10098.5663 | 502 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1087.4998 | 522 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 12.3 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 17.2 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.8 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 29.7 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.4 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 25.8 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 44.8 | 5.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 72.8 | 5.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.1 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.6 | 4.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 48.4 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.2 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.4 | 3.4 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.6 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 25.2 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 62.7 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 73.15 | 33 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4 | 4 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.3 | 5.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 8 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 8.4 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 15.3 | 5.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 26.4 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 51.6 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.2 | 3.2 | 2 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.4 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34.2 | 5.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.2 | 4.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 20.8 | 5.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10.6 | 5.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.2 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 64.8 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.4 | 5.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 11.6 | 5.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18.8 | 4.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.1 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.8 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 59.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 68 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.3 | 4.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.8 | 5.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21.5 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 23.6 | 5.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 25.2 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 44 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 8.8 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18.4 | 4.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 24.6 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 27.6 | 4.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 31.5 | 4.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 34.4 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 43.2 | 4.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 289.3832 | 179 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2953.8332 | 185 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 767.5 | 307 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 68.85 | 51 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 177.3333 | 76 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 24.0833 | 85 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1736.1333 | 116 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 33.7333 | 88 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 38 | 38 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 109.35 | 81 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152 | 152 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 96.6782 | 134.9 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 117.6966 | 113.9 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 245.8166 | 43 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2561.6666 | 100 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4891.25 | 559 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1635.6 | 564 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23089.8529 | 700.4 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3122.5166 | 43 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 5981.8 | 66 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 24.4833 | 13 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 381.1135 | 466.67 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21329.5831 | 721 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 60 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 304.2666 | 326 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 520.1998 | 459 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 424.8 | 18 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2291.6663 | 550 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 390.5833 | 43 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1432 | 30 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 455.26 | 700.4 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1169.5833 | 175 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3185 | 175 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1186.6664 | 400 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1984.8 | 18 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 154.5 | 45 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 150 | 5 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 650-Fluidized Bed
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | WECC | Off-Peak | 139.5 | 279 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 800-Miscellaneous
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3680.75 | 15 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 792.35 | 299 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 2207.2983 | 95.9 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 123.75 | 225 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 871.9332 | 164 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 1537.5666 | 95.6 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 864.7165 | 307 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 107.4 | 179 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 385 | 84 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 854.4832 | 307 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 83.8666 | 148 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 291.8833 | 211 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 775.5999 | 168 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Summer | 37.6 | 188 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3348 | 155 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 3019.185 | 152.1 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 729.4332 | 158 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 3001.5 | 135 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 585.825 | 160.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 88 | 160 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 584.8333 | 110 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 852 | CC steam units | NPCC | Winter | 264.3333 | 130 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 232.5332 | 128 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 981.7249 | 160.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | TRE | Summer | 870.8333 | 190 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1730 | Boiler explosion or implosion | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 59.3333 | 5 | 1 | 1 | 1730-Boiler explosion or implosion | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1661.3332 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.065 | 120.1 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1431.4164 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2473.333 | 560 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 423.4999 | 231 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 35.5 | 30 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 529.6249 | 334.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3.0833 | 37 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10024.1663 | 523 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U2-Forced - Delayed | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 364 | 280 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1780.35 | 429 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12446.5 | 730 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 60.4333 | 37 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 77.2 | 12 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 666.7332 | 274 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1386.3165 | 223 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 994.5 | 102 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1900 | 380 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 329.2464 | 379.9 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14421.3332 | 520 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 415.15 | 361 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 7513.7665 | 431 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 58.7666 | 86 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 169 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1907.5 | 35 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3217.5 | 110 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 890 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6359.12 | 548.2 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 481.2499 | 231 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 909.02 | 105.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 31.6665 | 380 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3762.9 | 339 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.82 | 171.76 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 734.25 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274.5333 | 232 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 34 | 30 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2141 | 60 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2465 | 197.2 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1431.8719 | 206.52 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22157.15 | 881 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 543.9066 | 171.76 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 697.9332 | 361 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 445 | 25 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 734.9999 | 450 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1780 | 178 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.5997 | 429 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.1665 | 410 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9519.5665 | 277 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 354.9832 | 361 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 173.4 | 102 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 650-Fluidized Bed
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 29.3333 | 10 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 650-Fluidized Bed
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 147.7332 | 277 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 34.4 | 48 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 176.9832 | 259 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 7737.75 | 543 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 96.8 | 33 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 102.9 | 49 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 129.1997 | 408 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 268.098 | 518.9 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2443.2332 | 283 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 84.8666 | 67 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 143.7333 | 49 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 141.4 | 101 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 57.8 | 34 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 69.3 | 33 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 46008 | 864 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 116.1 | 258 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 759 | 506 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 142.4 | 48 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 932.8 | 176 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 245.9166 | 227 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1068 | 178 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1812.6506 | 261.44 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 52.0833 | 62.5 | 2 | 2 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 1075.9666 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 656.2833 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 6526.6665 | 178 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 627.4665 | 208 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 695.7166 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 851 | CC GT units | MRO | Winter | 143.3332 | 215 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 47.6666 | 143 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Winter | 117.3332 | 176 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 503.5 | 95 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 980.304 | 141.39 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 852 | CC steam units | MRO | Winter | 106.6666 | 160 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 63.3333 | 95 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 32898.75 | 465 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 18.7998 | 282 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1525.3331 | 320 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1550 | 248 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 7 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4.6667 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 154.9998 | 300 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 35.5 | 106.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3.6667 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 1650 | 100 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 957 | 58 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 862-CoG steam units
1741 | Furnace and water gauge television auxiliary system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.3333 | 34 | 1 | 1 | 1741-Furnace and water gauge television auxiliary system | D1-Forced - Immediate | 100-Fossil-Steam
1741 | Furnace and water gauge television auxiliary system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 636 | 80 | 1 | 1 | 1741-Furnace and water gauge television auxiliary system | U1-Forced - Immediate | 100-Fossil-Steam
1741 | Furnace and water gauge television auxiliary system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1737.3333 | 80 | 1 | 1 | 1741-Furnace and water gauge television auxiliary system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.6 | 62 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2121.6666 | 100 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 24.1333 | 181 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 313.3333 | 25 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 523.25 | 161 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 398.35 | 31 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 857.5999 | 201 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 532.4999 | 450 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13789.6665 | 410 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4383.9998 | 240 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 56.35 | 69 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 124.2 | 69 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 172.8 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1720.8666 | 311 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2405.3999 | 171 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 309.5286 | 277.19 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 138.0166 | 169 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 430.3 | 26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1028.7499 | 75 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1784.4666 | 116 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 391.5166 | 169 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 953.4398 | 566.4 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.2333 | 223 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1029.1663 | 475 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3074.4996 | 645 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 698.7498 | 645 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2403 | 178 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11958.6333 | 178 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220.1619 | 213.06 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 325 | 250 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1796.3333 | 85 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 138.75 | 185 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4.5833 | 11 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 158.6 | 13 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 134.1525 | 178.87 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 498.0333 | 223 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 620.0333 | 178 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1567.0396 | 566.4 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7832 | 178 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 823.1998 | 504 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 865.1997 | 504 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 45.75 | 183 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 7541.6665 | 500 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.6666 | 49 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 916.6665 | 500 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 538.5 | 90 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 23300.3 | 41 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12276.6665 | 635 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5197.5 | 198 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 478.1497 | 393 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 102.6666 | 110 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 104.8332 | 170 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 366.9 | 18 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1923.1333 | 14 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 184.3 | 97 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 774 | 86 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432.15 | 201 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 358.5666 | 347 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5219.9991 | 1350 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8496.7164 | 469 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 40.3333 | 110 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 755.7667 | 14 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1266.6332 | 481 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8 | 20 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 102.6833 | 101 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7049.2667 | 41 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2108.4333 | 86 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1161 | 645 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3576.6664 | 740 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 333.5999 | 144 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 810.2664 | 412 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1487.6466 | 65.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.2499 | 166.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 520.5 | 90 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 185.9 | 143 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 277.4333 | 29 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6.9333 | 16 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 58.8999 | 186 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1233.9333 | 223 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 474.2331 | 347 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 931.1166 | 347 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 314.3331 | 410 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 988 | 190 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1560 | 240 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 47.2333 | 109 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 175 | 175 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 386.4 | 144 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 700.8499 | 393 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1870 | 850 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 766.3499 | 351 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1750.4667 | 44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 958 | 120 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2279.3332 | 526 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 752.2664 | 728 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1969.833 | 530 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 51.744 | 47.04 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1719.6665 | 268 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7.9167 | 12.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1800 | 400 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 6.2 | 12.4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 184 | 23 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 333.4666 | 82 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 160.65 | 81 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 3008.6333 | 106 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 36 | 40 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 16.6666 | 200 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 5.3333 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 10 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 20 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 17.9167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 29.75 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 30.3333 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 45.3333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 54 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 58.9167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 62.5 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 70.3333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 80.5 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 84.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 90.7667 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 94.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 100 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 100.6667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 108 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 6576.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 673.4 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Summer | 782.75 | 31 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 20.5833 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 28.0833 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 53.3167 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 60 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 64.8333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 65 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 83.8667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 89.95 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 94.1333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 94.2667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 102.8 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 112.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 13.4167 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 7.4667 | 7 | 2 | 2 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 10 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 11.25 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 15.25 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 32.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 44.3333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 53.9167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 66.5 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 67.75 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 70.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 83.75 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 84.4667 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 86.2667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 87.15 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 95.0667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 96.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 97.5 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 103.7333 | 8 | 1 | 2 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 105.4667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 106.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 109.4667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 116.8 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 134.8 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 5754.4667 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 103.6 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 379.75 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 1054.7333 | 26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 30.1667 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 22.25 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 42.5 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 49.35 | 7 | 1 | 2 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 72.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 79 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 86.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 101.7333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 121.1 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 122.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 128.8 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 134 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 54 | 90 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 211.5 | 90 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1.0833 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 20.6 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 27.8333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 40.8333 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 44.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 63.5833 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 64.6667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 71.6333 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 73 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 77.6667 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 83.1833 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 124.2667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 138.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 66.5 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 646.4667 | 2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 42.75 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 45.95 | 3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 60.9167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 65.9167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 68 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 68.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 71.3333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 82 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 82.2667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 86.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 93.0667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 97.4667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 108.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Winter | 318.6 | 27 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 78.234 | 21.24 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 308.5 | 2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 332.3833 | 37 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 12.4167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 30.5667 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 34 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 36.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 50.6333 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 53.0833 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 53.8667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 60.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 65.1 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 65.8667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 67.3333 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 73.3833 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 74 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 74.2667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 81.0833 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 82.3667 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 84.25 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 84.5333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 88.0833 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 89.1667 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 92 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 92.6667 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 98.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 118.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 120 | 20 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | NPCC | Winter | 29.25 | 27 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 15.4167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 40.4167 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 52.8333 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 74.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 74.4333 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 112.9333 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 117.6 | 8 | 2 | 3 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 126.4 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 556.715 | 30.9 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 864.7996 | 552 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 80.3 | 6 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 347.6666 | 28 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.75 | 151 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 90.5 | 15 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 978.9998 | 330 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3 | 10 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 38.4 | 12 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 164.2999 | 93 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | SF-Startup Failure | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1078 | 245 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 256.2666 | 248 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 181.0316 | 92.05 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 222.5449 | 284.1 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 125.8016 | 92.05 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 82.6666 | 248 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 27496.1664 | 457 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 223.1666 | 206 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 26361.2832 | 457 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 112.9333 | 88 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1392.09 | 284.1 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 419.1 | 381 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2041.2664 | 457 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 396.8 | 248 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 2046.2666 | 206 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 6874.3664 | 761 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 96.3332 | 170 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1034.4 | 72 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 284.4 | 72 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 680.5165 | 307 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 70.8332 | 170 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 699.6 | 72 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4 | 20 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4.6667 | 20 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 465.0516 | 180.02 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Winter | 1849.6 | 128 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Summer | 442.5 | 177 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 861-CoG GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 764.9999 | 270 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1070.6662 | 730 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1544.1332 | 313 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77199.633 | 871 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 584 | 730 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1545.6 | 448 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3000.7333 | 23 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3341.25 | 825 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 85.3333 | 160 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.72 | 25.05 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2419.5998 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 427.4999 | 135 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 77.4 | 258 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 400 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 515.8999 | 201 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 644.8331 | 730 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 104.25 | 45 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 650-Fluidized Bed
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 884 | 51 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6187.2797 | 379.2 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 34.8033 | 39.4 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 80.75 | 51 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 860-Co-generator Block
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 306.2498 | 525 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 205.3333 | 35 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 538.9166 | 145 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 47.4681 | 46.69 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 75.4468 | 74.21 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 26.481 | 16.38 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.75 | 15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3375.25 | 587 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1914 | 440 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 572.9 | 337 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2454.1 | 253 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 310.0833 | 61 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4946.4831 | 661 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 441.25 | 75 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 18.5925 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 85.8 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 463.3333 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679.9998 | 600 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.5 | 9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1805 | 190 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 2068 | 22 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2510.75 | 415 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1348.2999 | 417 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1837.333 | 530 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5020.6664 | 680 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4625.8329 | 650 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 48.6833 | 127 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 738.75 | 75 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1.5075 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 236.3 | 51 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.88 | 1.86 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.6666 | 230 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 275 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1313.9998 | 270 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1804.8332 | 221 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.5 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238.9665 | 214 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2778.7833 | 11 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 384 | 4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4693 | 60 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 887.3333 | 22 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6610.0666 | 263 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1372.2166 | 281 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1180.9 | 98 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12040.8831 | 311 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 727.05 | 393 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.8332 | 170 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 186 | 9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 260.7 | 237 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 368.8999 | 186 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.1665 | 410 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 512.9 | 223 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1279.5832 | 415 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3682.1998 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 969.9165 | 515 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1465.4 | 431 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2.01 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.9999 | 240 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.89 | 1.97 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.1667 | 50 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2184 | 13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 184.6532 | 251.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 28 | 14 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 566.9999 | 243 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 521.25 | 417 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4342.4991 | 1350 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23611.3329 | 662 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1198.0497 | 441 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 847.8166 | 169 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 656.2833 | 169 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 154.1108 | 63.77 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3009.435 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14168.9332 | 263.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 63.2231 | 291.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 634.883 | 343.18 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4119.2664 | 388 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 945.5874 | 206.31 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1142.6 | 116 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1510.4998 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1889.1329 | 659 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3961.4999 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 96.6666 | 58 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 32.96 | 16.48 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 49140.1498 | 747 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2977.7479 | 333.33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 359.05 | 43 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 787.5 | 125 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 145.6 | 28 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1795.7333 | 208 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 817.2865 | 570.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1756.0665 | 497 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5281.9997 | 417 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10484.9991 | 1350 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 754.4495 | 466.67 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2640 | 660 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5243.9331 | 661 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 726.7996 | 552 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 45.045 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2395.25 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345.7666 | 82 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 165.2666 | 134 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2688.4994 | 849 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12751 | 410 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1401.38 | 341.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 9.045 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2019 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 112.255 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 884.4 | 268 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 15379.3333 | 136 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 176.85 | 131 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 18.9933 | 25.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 800 | Miscellaneous | TRE | Summer | 494.1333 | 109 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 942.9333 | 208 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1303.75 | 15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 6370.8331 | 278 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 7953.3999 | 273 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 70 | 70 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 96.4 | 241 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1277.3 | 241 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 257.85 | 81 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1587.0832 | 325 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 127.1667 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 168.7 | 241 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1196.9665 | 241 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 14232.5832 | 505 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 15.1667 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 268.0333 | 236.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 80 | 80 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 964 | 60 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 173.3333 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 412.7666 | 122 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1261.3333 | 236.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 21.2419 | 98.04 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4236.4664 | 436 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 507.06 | 281.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 4185 | 310 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1430.8332 | 505 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 573.7596 | 537.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 38252.5 | 535 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 80.685 | 537.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 5213.1665 | 310 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1051.6 | 88 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 394.5332 | 538 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 47.136 | 78.56 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 199.7999 | 162 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 294.1499 | 166.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 521.7 | 141 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1163.9999 | 180 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1523.9999 | 180 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 3105 | 276 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | MRO | Summer | 243.04 | 156.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 345.0166 | 163 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 33 | 49.5 | 1 | 3 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 165.6 | 144 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1158.7332 | 191 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 5947.7666 | 218 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 41.1619 | 112.26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 56.13 | 112.26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 36.5366 | 109.61 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | TRE | Summer | 714.2083 | 152.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1890.2167 | 23 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 37.2295 | 106.37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 44.3208 | 106.37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 3515.4 | 279 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 246.9749 | 166.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 388.4833 | 163 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 319.2333 | 157 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Winter | 22.005 | 48.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Winter | 334.1332 | 179 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Summer | 320.34 | 213.56 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 397.6333 | 151 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 50.525 | 70.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 71.675 | 70.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 955.328 | 217.12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 325 | 60 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 18339.0833 | 229 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 829.45 | 313 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 27.065 | 54.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 924 | 210 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 17.7233 | 53.17 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 115.8666 | 158 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1228.9665 | 322 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 19.8476 | 54.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 225.8666 | 121 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 702.5 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D3 | Forced - Postponed | 2019 | Gas | GG | 852 | CC steam units | MRO | Winter | 32 | 16 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D3-Forced - Postponed | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 167.1399 | 164.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4.3333 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4.6667 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 222.5 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Summer | 117.6 | 72 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 6714.8999 | 243 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 113.112 | 282.78 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 2754.9999 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 65.0166 | 83 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 205.9666 | 167 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 47.25 | 21 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 264.9999 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 8 | 12 | 1 | 2 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 23.4 | 12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1421.2999 | 183 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 17.955 | 51.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 758.3333 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 3670.3332 | 286 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | MRO | Summer | 117.335 | 75.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 21.375 | 51.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 184.0166 | 90.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Summer | 209.3 | 322 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 101.7332 | 218 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 2876.4167 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 244.416 | 407.36 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 625.28 | 390.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | WECC | Summer | 127.3999 | 84 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 58 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 862-CoG steam units
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 10.5 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 33555.0832 | 427 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U2-Forced - Delayed | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3431.7833 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1347.3333 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 2546.5 | 22 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17575 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 2650.2 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1550.2167 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 574.5667 | 22 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 809.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1554.65 | 51 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3230.8333 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4374 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 6367.6667 | 20 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 437 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 818.75 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 896 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 253.3333 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1019.15 | 51 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3894.3666 | 43 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 789.25 | 33 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 930 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2046 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1319 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1775.3833 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2051.1 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 519.1333 | 26 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1392 | 24 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2039.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 5280 | 20 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1875.6 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 864 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1089.5833 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 9184 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 624 | 26 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1931.6167 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 651 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 806 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 674.3333 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 834.1667 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2480.4 | 36 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7257.25 | 55 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 832 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 139.4167 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 832 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3210.1 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 5290 | 20 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 282.6667 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 810 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2362.5 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 594 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2187.0833 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3009.1667 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 4698.65 | 33 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 840 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2010 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2591.6667 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 15500 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 246.4 | 4.48 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 323.0827 | 4.48 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 248.4 | 3.45 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5140.8 | 17.85 | 1 | 1 | 1810-Other boiler inspections | U1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14689.9999 | 339 | 1 | 1 | 1810-Other boiler inspections | U2-Forced - Delayed | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 684.4693 | 16.48 | 1 | 1 | 1810-Other boiler inspections | U1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 834.6667 | 20 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 800-Miscellaneous
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22623.3 | 243 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 291.9999 | 219 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 5495.4 | 18 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28.1666 | 169 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 15 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 113.66 | 56.83 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.1517 | 24.02 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 196.707 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208.9998 | 228 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 286.16 | 58.8 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 940.2666 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1075 | 86 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1153.7333 | 136 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1323 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2076.6665 | 356 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2244.8833 | 169 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2688 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4670.358 | 257.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163.1999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 255 | 10 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278.75 | 223 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 507.1 | 66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 808.4 | 172 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 842.2333 | 183.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3702.9437 | 520.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.5333 | 94 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 250.4 | 250.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 291.16 | 100.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2136 | 178 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2148.533 | 460.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2928.9387 | 24.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.822 | 51.72 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6511.8333 | 178 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 375.5499 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 516.7999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 144.9999 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 324.8 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 511.4666 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 128.8 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 185 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 391.88 | 97.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 742.3875 | 197.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10183 | 340 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30198.9129 | 700.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 135.7 | 69 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3454.2 | 108 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.3113 | 18.13 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 16 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.7499 | 171 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.1 | 159 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 271.32 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 492.2666 | 142 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1202.6666 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1907.5 | 218 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1958.4 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2220.9196 | 59.33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.65 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 290 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 296.6979 | 163.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 808.035 | 46.35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 962.8 | 58 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1530 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.3333 | 64 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 74.8 | 44 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.0333 | 26 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216.5625 | 41.25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 313.3876 | 54.82 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 542.6666 | 80 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1880.6666 | 248 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9776.1799 | 200.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 692.35 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1296.3999 | 168 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3618.7332 | 206 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4418.25 | 129 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2739.3332 | 140 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 20.3 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 216.2 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 47 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 82.6333 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 100.3 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 146.25 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 154.6999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.6667 | 25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20237.1661 | 790 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 40 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5805.3331 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.9333 | 22 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 150.5 | 70 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 379.9332 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 426.2666 | 278 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 426.6666 | 128 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1054.9333 | 46 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1328.4 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6083.0666 | 172 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11986.6666 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63114.6665 | 244 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.1333 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.9058 | 40.63 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 945.8166 | 121 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1052.6999 | 261 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1213.1512 | 41.57 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1316.5699 | 115.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1698.8506 | 168.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3449.248 | 210.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.6 | 33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 198 | 90 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.2 | 79 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3608 | 440 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5187.1166 | 257 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9002.7997 | 380.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14495.8333 | 71 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1122.1 | 147 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 137.7 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 187.6 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 590.15 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1160 | 145 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 137.5 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 672.5999 | 171 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 318.25 | 95 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 719.1 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1655.3073 | 257.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32673.5 | 505 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.4 | 22 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.9 | 82 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.39 | 18.13 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87 | 36 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185.4019 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 676.5512 | 18.13 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1012.5 | 45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1180.8 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1448.148 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1762.3498 | 279 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4884.55 | 107 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.1666 | 103 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.3333 | 130 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184.7066 | 158.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 214.016 | 133.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6999 | 114 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 501 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 744.2987 | 44.48 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50284.8 | 291 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.3953 | 38.29 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 123.05 | 69 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.9666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 804.6 | 108 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1538.25 | 293 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1750.5332 | 276.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2101.1999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 151.6999 | 111 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 159.5 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 260 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 173.6 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 210.8332 | 230 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 262.1666 | 65 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 59.5 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 133.4 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2138.4 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3807.2499 | 291 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D3-Forced - Postponed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10267.9998 | 255 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53227 | 340 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.5 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.1833 | 73 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.8395 | 18.21 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237.5 | 114 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.5 | 26 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 331.35 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 501.5 | 118 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 563.7333 | 151 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 806.4 | 256 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1022.5039 | 115.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1738.6452 | 210.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3281.8 | 244 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7149.9999 | 390 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27120 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.5 | 130 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.4666 | 52 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 234 | 78 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 554.4 | 126 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 589.5667 | 23 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 679.912 | 183.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1724.25 | 31.35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1822.8 | 62 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 160.2733 | 41.45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 442.1333 | 41.45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1539.9999 | 300 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1676 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3506.1165 | 211 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8579.6499 | 291 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1547.75 | 123 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 190 | 95 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 841.674 | 427.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 27.75 | 37 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 118.8999 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 157.5 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 177.8333 | 110 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 401.8666 | 137 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 604 | 80 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 176.0666 | 76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 367.3875 | 97.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 369.925 | 147.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2547 | 108 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 833.2665 | 431 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.3333 | 40 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.0166 | 49 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186.2655 | 53.99 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 251.4667 | 41 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 393.75 | 125 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 564.5332 | 146 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 679 | 140 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 695.5833 | 85 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1032 | 172 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1320 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2009.97 | 194.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3408.6 | 228 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4802 | 196 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7488.8332 | 262 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144.4913 | 118.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 219 | 73 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 254.9999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 295.1666 | 70 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2606.8699 | 187.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3485.8666 | 172 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.875 | 41.25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144 | 96 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2691.5807 | 263.45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3400.6722 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4023 | 298 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7688.8666 | 194 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 59.1833 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 884.4 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2704.1666 | 275 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5122.1666 | 73 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 151.25 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 451 | 205 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 190.4 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2545.9999 | 201 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 869.925 | 347.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 996.0591 | 277.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.7 | 89 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.9167 | 41 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.7333 | 77 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.1332 | 152 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187 | 51 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.4666 | 64 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 329.0933 | 96.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 796.25 | 91 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1041.6665 | 250 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1543.5 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2332.285 | 127.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3318.6666 | 131 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4204.2558 | 460.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13281.3333 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15279.7332 | 176 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15872.1465 | 567.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.7833 | 103 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 211.7866 | 133.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 317.5833 | 103 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 318.2666 | 248 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 572.2666 | 116 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 621.5591 | 41.95 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 713.7333 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2492.4 | 248 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.8333 | 10 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 129.1667 | 50 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.8233 | 45.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 542.2499 | 135 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 810 | 45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7734.3 | 58 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 244.3499 | 81 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 343.2 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 532.5 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 90.1 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 213.5 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 263.2 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 94.4166 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 17.5 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1239.85 | 247.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.3333 | 104 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.9875 | 18.13 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.7791 | 57.19 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354 | 118 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 380.3331 | 326 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 456.7333 | 62 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 870.4 | 128 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 893.55 | 161 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1611.4999 | 165 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1971.0902 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2156 | 196 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5898.88 | 567.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43.2 | 27 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 341.2035 | 60.39 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 698.25 | 133 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1185.1666 | 130 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1271 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.1397 | 38.57 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141 | 45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 526.5333 | 88 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1584.2 | 178 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7810.4 | 300.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8226.42 | 200.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4490.4333 | 214 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6390 | 135 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2182.647 | 427.97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 49.8333 | 130 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 105.75 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 257.3333 | 80 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 205.6333 | 31 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.98 | 18.33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17795.7665 | 307 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4414.1 | 74 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 71.5 | 14.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Winter | 126.1 | 19.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 514.8 | 14.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Other | BM | 800 | Miscellaneous | SERC | Winter | 67.275 | 19.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 28.12 | 140.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 19.6166 | 117.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 196.8682 | 274.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 787.08 | 187.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 171.405 | 263.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 285.1199 | 194.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 15.24 | 152.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 18.285 | 47.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 95.7598 | 302.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 46.5 | 186 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 53.31 | 177.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 174.3699 | 197.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 192.9233 | 186.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 52.6399 | 225.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 479.6765 | 190.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 13.12 | 262.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 17.2316 | 147.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 88.965 | 197.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1974.6998 | 294 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 10.6666 | 320 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 90.9332 | 176 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 44.6399 | 167.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3044.8166 | 299 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 32.1531 | 275.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 108.2999 | 171 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 144.5332 | 271 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 233.9449 | 197.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | SERC | Summer | 9261.6 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 851 | CC GT units | WECC | Summer | 189.8 | 73 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U2 | Forced - Delayed | 2019 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 5696.8333 | 190 | 2 | 2 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 29375 | 470 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 122.4498 | 237 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 109.2 | 42 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | SERC | Winter | 16505.0999 | 162 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 35.0583 | 150.25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 1591.4932 | 322.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 6688.5732 | 322.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 62.9332 | 236 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U2 | Forced - Delayed | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2036.6665 | 235 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 6601.4666 | 77 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | WECC | Winter | 121.05 | 269 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 852 | CC steam units | RFC | Winter | 940.9165 | 322.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 176.3667 | 11 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 860-Co-generator Block
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2019 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 418.5 | 186 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 861-CoG GT units
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2019 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 137.25 | 61 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 862-CoG steam units
1900 | Improper balance between tube sections not due to fouling or plugging | Boiler | Boiler Design Limitations | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.8332 | 155 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | D2-Forced - Delayed | 100-Fossil-Steam
1900 | Improper balance between tube sections not due to fouling or plugging | Boiler | Boiler Design Limitations | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.9999 | 180 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | D2-Forced - Delayed | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 9 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 278.7 | 9 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3575.88 | 7.56 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1.8667 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 824.7 | 18 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 501.9667 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2090.156 | 5.82 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 22372 | 80 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 43.5 | 6 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7435.05 | 73 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1147.44 | 6.83 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2504.5643 | 22.22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 601.0667 | 7 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.0833 | 19 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11662.5667 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 15 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1039.8667 | 44 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2580.9 | 18 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 12529.6833 | 31 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6954.1333 | 59 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10549.1666 | 50 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 25846.8 | 51 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 486.7496 | 531 | 1 | 1 | 1910-Inadequate air not due to equipment problems | U1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2829.7833 | 31 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.5167 | 7 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7243.496 | 13.26 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 433.3663 | 36.83 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1236.4 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3150.834 | 9.64 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 66 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.05 | 9 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 808.486 | 7.31 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 862.125 | 8.55 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1575.36 | 21.88 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2447.5 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4337.4167 | 23 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12226.545 | 24.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 615.6 | 19 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2418.5883 | 7.37 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2673.3443 | 6.58 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13478.4 | 18.72 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1084.8333 | 23 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4549.4598 | 20.51 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11250.4 | 20.09 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 72.1333 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 162.8 | 33 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 664.6667 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1200.7333 | 28 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11371.2 | 23 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 34997.85 | 27 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 7 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.6 | 4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2358.72 | 10.92 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5887.5667 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1.3333 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1643.75 | 15 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4606.2492 | 16.15 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 826.14 | 17.64 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 53.0833 | 7 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 238 | 12 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 259.9667 | 11 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5291 | 37 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7989 | 36 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.65 | 9 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 538.8327 | 20.54 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1121.0737 | 16.43 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5182.65 | 27 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.84 | 4.21 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1018.7917 | 4.99 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2055.5352 | 6.53 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3192 | 6.65 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6176 | 9.65 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1587.8 | 17 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6904.32 | 17.98 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 58.25 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 33505.7833 | 73 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2150.7625 | 10.95 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117 | 6.5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 354.9 | 18 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3408.2833 | 47 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9.75 | 13 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5934.72 | 8.43 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3206.88 | 22.27 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 878.3333 | 34 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5392.8 | 54 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9741 | 102 | 1 | 1 | 1980-Boiler safety valve test | U1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 35 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 194.75 | 95 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.0793 | 5.18 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 471.8333 | 38 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 458.4997 | 393 | 1 | 1 | 1980-Boiler safety valve test | U1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 289.3333 | 35 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3384 | 288 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4654.25 | 15 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 151.64 | 37.91 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 650-Fluidized Bed
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 0.78933 | 0.64 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 650-Fluidized Bed
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 80.9813 | 37.96 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 650-Fluidized Bed
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 308.5333 | 178 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 875 | 125 | 1 | 4 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D2-Forced - Delayed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 355.2497 | 435 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 562.2164 | 427 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 599.0831 | 395 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5234.3331 | 410 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 780.7666 | 118 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1278 | 213 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 710 | 355 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D2-Forced - Delayed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.5 | 9 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 399.9666 | 169 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 595.8666 | 164 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1119.65 | 457 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1593.75 | 255 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2351.6665 | 425 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3211 | 247 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3451 | 493 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3996.4 | 412 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.05 | 9 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4000 | 400 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.7 | 9 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 750.2 | 66 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1715.1999 | 201 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2070.8332 | 355 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3905.4165 | 455 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 417.05 | 439 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 424.4333 | 238 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 529.8332 | 289 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3660.6164 | 451 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5052 | 421 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9112.5 | 405 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9256 | 178 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.0833 | 71 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.8333 | 70 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351 | 390 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472.15 | 133 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 742.0497 | 459 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 994.2163 | 493 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1002.0832 | 481 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2526.9999 | 210 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31365 | 510 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3606.3329 | 620 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D2-Forced - Delayed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 525.55 | 457 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 736.2498 | 465 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1386.8666 | 142 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1714.3331 | 278 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3735.0664 | 436 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4050 | 324 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.7833 | 79 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450 | 40 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 533.3332 | 128 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 971.5833 | 89 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1186.8 | 276 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1532.0664 | 469 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1701 | 243 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3476.2 | 382 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4145.7332 | 472 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4388.6664 | 454 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.2663 | 496 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1428.8 | 304 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2784.7499 | 423 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4960.2664 | 418 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.1667 | 10 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 3 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 900.5833 | 101 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.0667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.605 | 12.33 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8732.9 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 630 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 5.4667 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 241.5 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 7 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 242 | 8.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 81.6666 | 175 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 751.6666 | 164 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16200.4166 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 1 | 4 | 7 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 1.5 | 11 | 29 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.51 | 1.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.6 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 7 | 9 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 2 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.2 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.81 | 2.09 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.02 | 1.82 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.02 | 2.86 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 2.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.89 | 1.43 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.02 | 3.78 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 2.8 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.99 | 1.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.01 | 1.67 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1.75 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.9 | 4.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.02 | 2.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 2.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.01 | 5.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.95 | 1.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.9 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.96 | 2.08 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.07 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.88 | 1.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.4 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.88 | 1.88 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.3 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.6 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.5 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 3 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.39 | 1.13 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.5 | 1.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.61 | 1.87 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.8 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.28 | 1.82 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.8 | 1.76 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.91 | 2.97 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.6 | 4.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24 | 4.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.6 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.2 | 4.15 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.62 | 5.77 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35 | 1.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.2 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.8 | 16.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115760.6665 | 494 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2757.333 | 440 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7596.9925 | 20.55 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 896.933 | 434 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1073.9166 | 245 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28299.2 | 736 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U3 | Forced - Postponed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 139742.8664 | 427 | 1 | 1 | 1999-Boiler; miscellaneous | U3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 227.4 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 23.4 | 5.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 21314.5 | 47 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 856.9 | 66 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2970 | 165 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 2.5 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.1 | 1.7 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 6 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.99 | 2.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.1 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 3.25 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.98 | 2.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 14 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.2 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.01 | 2.43 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 5.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.9 | 7.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.02 | 1.39 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.03 | 1.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29 | 7.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.6 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.15 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 4.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 509.86 | 13.78 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.99 | 3.33 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.01 | 3.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.6467 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 2.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.98 | 2.07 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.95 | 3.45 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.91 | 3.89 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.4 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.7 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.2 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.7 | 2.85 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.8 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13 | 3.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.1 | 2.82 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.12 | 1.89 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.6 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.96 | 1.84 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.5 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 320.1666 | 170 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2019 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 5297.325 | 642.1 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.5 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.84 | 62.4 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 22.9333 | 43 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1 | 1 | 3 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 809.71 | 10.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1518 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 819 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1539.6 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 466.62 | 33.33 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 9 | 35 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 1 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.98 | 1.18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.1 | 3.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.39 | 4.49 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.2 | 1.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 7 | 17 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 1.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.03 | 3.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 3.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 4.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.92 | 3.94 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 415.9166 | 115 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 760 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.7 | 0.7 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1 | 0.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1 | 5 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1.5 | 6 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.4 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5 | 5.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 7 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.08 | 1.26 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.1 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.83 | 1.53 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.8 | 5.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 10.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.36 | 1.72 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.01 | 1.77 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.2 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.56 | 3.32 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.8 | 2.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.97 | 1.39 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.99 | 3.09 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2987.6 | 66 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4570 | 200 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25839.45 | 819 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2463.6665 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4639.1667 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 1 | 2 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.0333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 1 | 2 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4751.85 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 4 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 530.4 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 22.3833 | 15.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 15.4166 | 185 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 134992 | 286 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 1 | 11 | 76 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.99 | 1.33 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.01 | 1.67 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.1 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.8 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.96 | 1.12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 1 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 2.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 1.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.99 | 6.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 4.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.98 | 1.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.7183 | 3.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.99 | 3.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.01 | 1.63 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 9 | 44 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 2.5 | 2 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.8 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 5.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17 | 3.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.02 | 2.86 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.01 | 3.43 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.1 | 8.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.9 | 4.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.3 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.6 | 0.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.1 | 5.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.12 | 1.02 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.98 | 1.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.6167 | 0.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.68 | 1.52 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.6 | 7.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.26 | 2.14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.53 | 2.79 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.97 | 2.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.39 | 3.77 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3638.3665 | 434 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35081.6665 | 434 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 300.5511 | 346.79 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 558 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 89.4 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 574.275 | 11.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 43.9999 | 165 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 676.8666 | 284 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 19987.5 | 390 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.1 | 0.55 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 11 | 60 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 3.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 2.5 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.8 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 2.5 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.99 | 5.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.03 | 2.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.95 | 1.53 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.04 | 2.56 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.6 | 1.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41 | 4.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3346.6664 | 800 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1 | 1 | 10 | 74 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 2.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.06 | 1.22 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.4 | 0.7 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.19 | 0.73 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.8 | 0.76 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.99 | 1.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.8 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.68 | 1.42 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.7 | 1.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.5 | 3.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.99 | 2.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.8 | 0.65 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.1 | 2.02 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 2.4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17 | 4.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.22 | 1.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.5 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.1 | 2.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.7 | 31.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.14 | 3.74 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.52 | 1.59 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48 | 12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 589 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 160.2 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 199389.7999 | 411 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70048 | 440 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.0167 | 19 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.8333 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.5167 | 7.55 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 408.2667 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 2007.6 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 111.725 | 10.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 204.6 | 36 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 4 | 5 | 6 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.8 | 1.2 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 2 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.99 | 3.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.96 | 3.12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.96 | 2.36 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.5 | 1.5 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 2.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.99 | 2.33 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 2.2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.94 | 1.21 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.7 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.9 | 7.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23 | 11.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.2 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.8 | 2.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.9 | 0.9 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1 | 1 | 9 | 25 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.1 | 1.1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.2 | 1.2 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.2 | 0.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.5 | 0.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.9 | 1.18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.99 | 3.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.16 | 2.77 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.52 | 2.94 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.51 | 2.41 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.59 | 1.79 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.24 | 2.18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.69 | 3.13 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.3 | 2.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.6666 | 70 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1808.8 | 112 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.6665 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1065706.1664 | 830 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1430 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1121.1665 | 434 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5811.6666 | 110 | 2 | 2 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 11 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2806.4 | 32 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 232.5 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 335.4166 | 125 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 396.11 | 36.01 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 454.75 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1241 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 17.68 | 10.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2019 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 743.7 | 111 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.8 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 3 | 9 | 21 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.9 | 1.3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 1.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.98 | 1.83 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 1 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.96 | 1.62 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.99 | 4.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.99 | 2.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.9 | 6.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8 | 5.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.03 | 3.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.96 | 3.62 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.04 | 3.42 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 2.4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.9 | 2.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.08 | 2.06 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41 | 2.05 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2019 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam