## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of EVENT_COUNT | Sum of DISTINCT_UNITS | Sum of MWLost | Sum of MWHrsLost
0000-Reserve shutdown | 2 | 1 | 172.8 | 771.8399
0010-Thaw shed failure or fire | 1 | 1 | 17 | 119
0020-Coal car dumpers; shakers; and unloaders | 2 | 2 | 320 | 1637.4999
0022-Unloading/receiving hopper (train/truck) | 1 | 1 | 17 | 37.9667
0024-Rotary plow | 2 | 2 | 47 | 162.9833
0028-Dust collection system | 6 | 6 | 929.23 | 11216.031
0030-Coal conveyors and feeders | 178 | 178 | 40778.64 | 2352527.0111
0035-Metal detector/collector (including magnetic separator) | 2 | 2 | 282.21 | 476.2498
0040-Coal elevators | 1 | 1 | 100 | 330
0050-Coal storage fires | 4 | 4 | 1840 | 16093.3325
0060-Coal crushers including motors | 15 | 15 | 2677 | 25736.4161
0075-Storage silos/hoppers | 20 | 20 | 4414 | 29724.7152
0080-Stackers/reclaimers | 26 | 26 | 571.62 | 2735.6405
0084-Coal conveyor scales-storage coal pile | 4 | 4 | 860 | 877.9997
0085-Bunker feeder coal scales | 1 | 1 | 839 | 66714.4828
0090-Bunker fires | 8 | 8 | 2407.25 | 419871.0576
0095-Bunker flow problems | 126 | 123 | 6211.58 | 35575.5255
0100-Bunker gates | 8 | 8 | 254.68 | 9673.5199
0105-Bunker structures | 1 | 1 | 31.3 | 940.565
0106-Coal drying system (see additional codes 0125-0127) | 1 | 1 | 202 | 2424
0107-Screen (prior to bunkers) | 3 | 3 | 114 | 448.8333
0110-Other coal fuel supply problems up through bunkers | 29 | 29 | 6533.14 | 55609.911
0111-Solid fuel feeder conveyors | 115 | 115 | 1622.46 | 22421.8878
0114-Solid fuel volumetric feeder | 23 | 23 | 152.2 | 602.9
0115-Solid fuel gravimetric feeder | 5 | 5 | 137 | 764.4666
0116-Solid fuel feeder motors | 4 | 4 | 49.43 | 193.5967
0121-Other solid fuel feed problems | 22 | 22 | 506.04 | 2695.6211
0127-Other coal crusher dryer problems (see code 0106) | 1 | 1 | 183 | 1967.25
0129-Other coal processing system problems | 7 | 7 | 1382.3 | 3569.3327
0139-Sorbent handling drying equipment | 2 | 2 | 246 | 785.1498
0162-Bed material conveyors A | 2 | 2 | 12.52 | 349.0667
0163-Bed material feeders | 2 | 2 | 18.6 | 1541.475
0174-Other bed material handling equipment | 3 | 3 | 86 | 47.8333
0200-Pulverizer exhauster fan (for indirect firing) | 9 | 9 | 706 | 10508.4832
0205-Pulverizer exhauster fan drive | 24 | 24 | 1374.8 | 43161.133
0240-Pulverized coal bin | 30 | 30 | 6299.26 | 16960.0953
0250-Pulverizer feeders | 963 | 960 | 116537.11 | 975994.2681
0253-Pulverizer feeder motor | 35 | 35 | 4389 | 169791.4118
0255-Pulverizer feeder coal scales | 13 | 13 | 1028.53 | 18284.9927
0256-Seal air system (air to pulverizers) | 7 | 7 | 961.8 | 7245.4528
0257-Coal Crusher/dryer between feeder and pulverizer | 3 | 3 | 354.76 | 734.2099
0260-Primary air fan | 98 | 98 | 19952.55 | 402714.0384
0262-Primary air fan lube oil system | 4 | 4 | 1031 | 3587.2327
0263-Primary air fan drives | 36 | 36 | 5119.41 | 185453.3223
0264-Other primary air fan problems | 20 | 20 | 3508.83 | 65988.4446
0265-Primary air heater | 5 | 5 | 702.8 | 74616.6998
0266-Primary air heater fouling | 1 | 1 | 422 | 2574.2
0267-Primary air flow instrumentation | 37 | 37 | 3971.15 | 29612.0168
0270-Primary air duct and dampers | 107 | 107 | 15029.39 | 258616.2248
0280-Pulverizer fires | 39 | 39 | 4999 | 104748.7985
0290-Pulverizer reduced capacity due to wear | 2 | 2 | 33 | 346.1667
0300-Pulverizer motors and drives | 92 | 92 | 8748.38 | 338308.2321
0310-Pulverizer mills | 738 | 738 | 75248.34 | 1325792.7431
0312-Pulverizer mill classifiers | 43 | 43 | 4256.62 | 127948.1449
0313-Pulverizer mill trunnion seals | 6 | 6 | 1001.66 | 5096.965
0315-Pulverizer mill coal level controls | 1 | 1 | 415 | 498
0320-Foreign object in Pulverizers mill | 53 | 53 | 3419.39 | 62433.7096
0325-Pulverizer skidding | 7 | 7 | 802.2 | 43987.8463
0330-Pulverizer coal leak (pulverizers only) | 116 | 115 | 11428.9 | 88979.0893
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 42 | 42 | 4139.92 | 20719.4234
0335-Pulverizer lube oil system | 109 | 109 | 11015.58 | 60609.8613
0338-Pulverizer control systems (temperature and pressure) | 35 | 35 | 3580.87 | 18902.5147
0339-Pulverizer System Puff | 5 | 5 | 1168 | 65388.8665
0340-Other pulverizer problems | 233 | 233 | 31244.09 | 295512.1312
0342-Pulverizer inert system | 8 | 8 | 1320.02 | 12126.0651
0344-Pulverizer inspection | 32 | 32 | 2956.97 | 130612.5025
0345-Pulverizer overhaul | 18 | 18 | 1069.37 | 173053.8547
0346-Pulverizer pyrite removal system | 102 | 102 | 10275.12 | 40536.8697
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 44 | 44 | 4646.6 | 40112.8751
0358-Oil burner piping and valves | 11 | 11 | 5353 | 5694.5154
0359-Gas burner piping and valves | 101 | 101 | 12830.94 | 270527.4926
0360-Burners | 106 | 105 | 10661.34 | 614134.0114
0370-Burner instruments and controls (except light-off) | 108 | 106 | 14165.16 | 128838.9029
0380-Light-off (igniter) systems (including fuel supply) | 48 | 48 | 6230.94 | 41689.4468
0385-Igniters | 55 | 54 | 10003.89 | 70792.2704
0390-Burner wind boxes and dampers | 8 | 8 | 2253 | 3989.3487
0400-Burner wind box fires | 4 | 4 | 1536 | 90650.3159
0410-Other burner problems | 35 | 35 | 3014.34 | 162523.6896
0415-Cyclone feeders | 34 | 34 | 1696.97 | 26669.7196
0420-Cyclone crusher | 12 | 12 | 549 | 11348.2999
0425-Cyclone dampers | 1 | 1 | 25 | 3.75
0426-Cyclone air ducts | 3 | 3 | 171 | 129.1666
0430-Cyclone furnace | 11 | 11 | 2025.34 | 26397.9091
0435-Other cyclone problems | 224 | 166 | 9875.03 | 245019.9069
0440-Fuel oil pumps (general) | 3 | 3 | 633.7 | 3750.3663
0441-Fuel oil pumps (burner supply) | 4 | 4 | 671.1 | 1639.1596
0442-Fuel oil pumps (forwarding/transfer) | 2 | 2 | 1130 | 2128.1663
0460-Fuel oil atomizers | 5 | 5 | 140 | 171.9167
0470-Oil and gas fires | 4 | 4 | 713 | 2178.2914
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 57 | 57 | 12424.71 | 473045.025
0500-Main steam piping up to turbine stop valves | 23 | 23 | 4366.96 | 497335.2054
0510-Main steam relief/safety valves off superheater | 26 | 26 | 2799.73 | 86623.8158
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 56 | 56 | 12853.9 | 644856.1371
0530-Other main steam system problems | 44 | 44 | 7929.43 | 103340.4861
0540-Hot reheat steam piping up to turbine stop valves | 24 | 24 | 6765.82 | 446030.1879
0541-Cold reheat steam piping up to boiler | 13 | 13 | 2355.65 | 57757.6248
0550-Reheat steam relief/safety valves | 29 | 29 | 6883.7 | 134485.7525
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 38 | 38 | 7716.71 | 490987.2393
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 14 | 14 | 2443.9 | 42626.4823
0570-Other reheat steam problems | 29 | 29 | 5461.24 | 663927.1081
0580-Desuperheater/attemperator piping | 13 | 13 | 3139.46 | 78574.0121
0590-Desuperheater/attemperator valves | 40 | 40 | 9887.52 | 188724.1257
0610-Desuperheater/attemperator drums | 1 | 1 | 635 | 1513.4165
0620-Other desuperheater/attemperator problems | 7 | 7 | 1548.89 | 50026.0035
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 4 | 4 | 1961 | 131376.532
0640-Startup bypass system valves | 22 | 22 | 12647 | 257615.0278
0650-Startup bypass tanks or flash tanks | 2 | 2 | 2061 | 165157.4164
0660-Other startup bypass system problems | 1 | 1 | 198 | 3369.2999
0670-Feedwater piping downstream of feedwater regulating valve | 7 | 7 | 1612 | 40592.6666
0680-Feedwater valves (not feedwater regulating valve) | 29 | 29 | 6719.89 | 182109.6249
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 7 | 7 | 1814 | 61836.4396
0700-Blowdown system valves A | 10 | 10 | 1208.7 | 1722.3331
0710-Blowdown system piping B | 9 | 9 | 1522.96 | 36857.7326
0720-Blowdown system controls / instrumentation | 1 | 1 | 246.3 | 291.4549
0730-Other blowdown system problems | 3 | 3 | 1143 | 3673.0493
0740-Boiler recirculation pumps | 23 | 23 | 6501.41 | 406601.1708
0741-Boiler recirculation pumps - motors | 17 | 17 | 3211.1 | 510649.3322
0742-Boiler recirculation pumps - motors - cooling system | 4 | 4 | 1635 | 30372.4993
0750-Boiler recirculation piping including downcomers | 2 | 2 | 848 | 490454.9331
0760-Boiler recirculation valves | 13 | 13 | 7054.28 | 64808.2184
0770-Other boiler recirculation problems | 6 | 6 | 1506.6 | 8452.7078
0775-Economizer piping | 25 | 25 | 3587.83 | 322040.0375
0780-Headers between tube bundles | 7 | 7 | 1702 | 157144.6748
0782-Headers and caps | 6 | 6 | 930 | 349861.7664
0790-Pipe hangers; brackets; supports (general) | 1 | 1 | 57 | 685.9
0799-Other miscellaneous piping system problems | 24 | 24 | 3559.6 | 135331.7416
0800-Drums and drum internals (single drum only) | 49 | 48 | 10674.38 | 308848.1186
0801-HP Drum (including drum level trips not attributable to other causes) | 117 | 117 | 19421.21 | 232945.4082
0802-IP Drum (including drum level trips not attributable to other causes) | 54 | 54 | 10844.81 | 26761.3819
0803-LP Drum (including drum level trips not attributable to other causes) | 26 | 26 | 3900.89 | 19760.627
0810-Boiler supports and structures (use code 1320 for tube supports) | 5 | 5 | 1399 | 923607.8995
0820-Casing | 24 | 24 | 6341.46 | 1329024.4307
0830-Doors | 31 | 31 | 9119.6 | 334527.3876
0840-Refractory and insulation | 10 | 10 | 1476.5 | 308563.9325
0848-Inlet panel | 3 | 3 | 226.4 | 819.0633
0850-Other internal or structural problems | 15 | 15 | 2424.94 | 180856.1258
0855-Drum relief/safety valves (Single drum only) | 26 | 26 | 4317.81 | 278990.4171
0856-HP Drum relief/safety valves | 1 | 1 | 88 | 26.4
0857-IP Drum relief/safety valves | 1 | 1 | 115.3 | 1118.41
0859-Tube external fins/membranes A | 4 | 4 | 759 | 30273.7999
0860-Soot blowers - air (see code 3844 for air delivery system) | 8 | 8 | 712 | 1369.6333
0870-Soot blowers - steam | 25 | 25 | 2412.5 | 64930.3267
0873-Soot blower drives | 3 | 3 | 300 | 4300.25
0876-Soot blower controls | 21 | 21 | 2906.13 | 33193.3947
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 33 | 32 | 4115.71 | 104548.6453
0885-Fly ash Removal System - wet transport | 3 | 3 | 372.3 | 15867.6615
0890-Bottom ash systems (wet or dry) | 180 | 179 | 10146.71 | 554701.0645
0891-Bottom ash hoppers (including gates) | 28 | 28 | 5241.74 | 162120.0645
0892-Bottom ash clinker grinders | 19 | 19 | 5078 | 306798.099
0894-Bottom ash piping and valves | 7 | 7 | 1168.8 | 30271.7999
0895-Ashpit trouble | 2 | 2 | 241 | 40422
0896-Bottom ash dewatering bin system; instruments and controls | 3 | 3 | 1260 | 54196.1332
0897-Bottom ash rotary (drag chain type) conveyor and motor | 69 | 69 | 21447.95 | 714725.18
0898-Bottom ash pyrite hopper (pulverizer reject) system | 1 | 1 | 129 | 924.4999
0899-Bottom ash controls and instrumentation | 3 | 3 | 562 | 1682.9331
0900-Slag-tap (cyclone furnace) | 13 | 13 | 988.33 | 53452.6788
0920-Other slag and ash removal problems A | 107 | 85 | 21051.11 | 355469.8085
0930-Bed material coolers | 2 | 2 | 386 | 48592.2166
0933-Bed material fans/blowers | 1 | 1 | 233 | 966.95
0934-Bed material fan/blower motors | 1 | 1 | 102 | 83.2999
0936-Bed material conveyors B | 2 | 2 | 21 | 208.5
0950-Other bed material system problems | 7 | 7 | 1616.6 | 29722.8362
0960-Char transport piping and valves | 2 | 2 | 35.4 | 1880.77
0980-High pressure loop seal recirculation fans/blowers | 2 | 2 | 233 | 3635.1666
0982-High pressure loop seal recirculation fan/blower controls | 1 | 1 | 30 | 404.5
0989-Other bed solids recirculation problems | 5 | 5 | 379.36 | 95386.5873
0990-Refractory | 4 | 4 | 323 | 10717.3166
0991-Tube leaks | 13 | 13 | 904.58 | 160306.1846
0999-Other heat exchanger problems | 1 | 1 | 90 | 1543.5
1000-Waterwall (Furnace wall) | 499 | 499 | 152182.99 | 12765685.8116
1003-Steam generating tubes between steam drum and mud drum | 13 | 13 | 2678.19 | 158209.1441
1005-Generating tubes | 33 | 33 | 2752.65 | 379878.8368
1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | 2 | 2 | 194.2 | 24213.7665
1010-Cyclone furnace (in cyclone area only) | 17 | 17 | 6384.03 | 653565.444
1020-Convection pass wall (water tubes only) | 17 | 17 | 5308.13 | 405670.9496
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 11 | 11 | 2620.3 | 233798.5777
1035-Platen superheater | 35 | 35 | 18828.23 | 2086679.5639
1040-First superheater | 99 | 99 | 28878.73 | 3238712.9686
1050-Second superheater | 134 | 134 | 49565.03 | 4141830.2743
1055-External superheater link tubing | 2 | 2 | 685 | 40185.3333
1060-First reheater | 94 | 94 | 44341.02 | 4209448.4472
1070-Second reheater | 21 | 21 | 8263.77 | 829563.2974
1075-External reheater link tubing | 4 | 4 | 918 | 49687.6497
1080-Economizer | 122 | 122 | 32215.94 | 2685362.304
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 10 | 10 | 3103 | 219573.882
1090-Other boiler tube leaks | 152 | 152 | 38669.87 | 4074183.3749
1100-Waterwall (Furnace wall) | 50 | 50 | 7738.81 | 1018439.5787
1103-Steam generating tubes between steam drum and mud drum | 2 | 2 | 10.53 | 1803.1925
1105-Generating tubes | 7 | 7 | 782.5 | 60716.5097
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 1 | 1 | 395 | 24206.9165
1140-First superheater | 9 | 9 | 1502.4 | 92434.2595
1150-Second superheater | 23 | 20 | 5605.44 | 156695.037
1160-First reheater | 20 | 20 | 2708.57 | 141709.1554
1170-Second reheater | 6 | 6 | 945.1 | 48699.6128
1180-Economizer | 11 | 11 | 1452.31 | 162492.4344
1190-Other tube slagging or fouling | 34 | 34 | 3251.33 | 186980.1764
1191-Bed agglomeration (FBC only) | 4 | 4 | 150 | 7953.125
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 80 | 80 | 5106.2 | 348885.2424
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 10 | 10 | 4262 | 36424.6988
1300-Water side fouling | 2 | 2 | 387 | 55280.1999
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 3 | 3 | 458 | 117448.4831
1310-Water side cleaning (acid cleaning) | 1 | 1 | 110 | 6138
1320-Tube supports/attachments | 2 | 2 | 382.2 | 7954.0565
1340-Tube modifications (including addition and removal of tubes) | 3 | 3 | 282 | 17782.2166
1350-Other miscellaneous boiler tube problems | 14 | 14 | 2356.89 | 470916.743
1360-Boiler drains system | 8 | 8 | 2128.74 | 81734.1747
1400-Forced draft fans | 139 | 139 | 16665.33 | 2280264.1365
1401-Forced draft fan dampers | 37 | 37 | 8334.65 | 84878.7719
1407-Forced draft fan lubrication system | 7 | 7 | 2455 | 26986.6994
1410-Forced draft fan motors | 53 | 53 | 10080.75 | 1109872.0513
1411-Forced draft fan motors - variable speed | 23 | 23 | 4415.23 | 75659.9117
1412-Forced draft fan drives (other than motor) | 24 | 24 | 5008.7 | 92035.8655
1413-Forced draft fan couplings | 13 | 13 | 3173.9 | 247518.8325
1415-Forced draft fan controls | 58 | 55 | 10519.14 | 102837.5712
1420-Other forced draft fan problems | 41 | 41 | 7941.7 | 332332.0214
1421-Secondary air fans/blowers | 7 | 7 | 739.7 | 93979.8763
1422-Secondary air fan/blower motors - single speed | 4 | 4 | 377.7 | 37932.795
1424-Secondary air fan/blower controls | 2 | 2 | 828 | 5838.8331
1430-Air supply ducts from FD fan | 7 | 7 | 2137.8 | 642883.0945
1431-Air supply dampers from FD fan | 4 | 4 | 177.3 | 4115.3783
1432-Air supply duct expansion joints | 4 | 4 | 1217.31 | 81103.9999
1440-Air supply dampers | 17 | 17 | 2686.64 | 100734.989
1450-Other air supply problems | 79 | 79 | 9315.35 | 486171.1536
1455-Induced draft fans | 471 | 469 | 39079.57 | 2304474.2524
1456-Induced draft fan dampers | 46 | 46 | 7520.22 | 191951.2105
1457-Induced draft fan lubrication systems | 25 | 25 | 5061.08 | 35070.3981
1460-Induced draft fan fouling | 44 | 44 | 3532.97 | 469765.4192
1470-Induced draft fan motors and drives | 107 | 107 | 17444.62 | 1956369.7091
1471-Induced draft fan motors - variable speed | 60 | 60 | 13178.61 | 210285.3349
1472-Inducted draft fan coupling | 6 | 6 | 1525.55 | 250299.9345
1475-Induced draft fan controls | 95 | 95 | 16667.23 | 393699.0779
1476-Induced draft fan speed changer | 12 | 12 | 2065 | 42167.9327
1480-Other induced draft fan problems | 103 | 103 | 20424.15 | 502532.5726
1487-Air heater (tubular) | 7 | 7 | 568.3 | 33896.2665
1488-Air heater (regenerative) | 112 | 112 | 19945.72 | 2349018.4491
1489-Air heater (heat pipe; plate-type) | 9 | 9 | 2493 | 169759.049
1492-Air heater fouling (tubular) | 3 | 3 | 32.54 | 65079.04
1493-Air heater fouling (regenerative) | 46 | 41 | 1404.23 | 154194.2238
1495-Other air heater fouling (heat pipe; plate-type) | 2 | 2 | 61.3 | 6519.3
1500-Air heater soot blowers | 1 | 1 | 23 | 1082.9167
1510-Flue gas ducts (except recirculation) | 5 | 5 | 406 | 7516.7165
1512-Flue gas expansion joints | 10 | 10 | 2747.97 | 246167.0186
1520-Flue gas dampers (except recirculation) | 8 | 8 | 1340 | 64475.1661
1530-Other flue gas problems | 13 | 13 | 2545.55 | 99053.7148
1535-Flue gas recirculating fan | 8 | 8 | 2781.7 | 195579.6334
1536-Flue gas recirculating fan dampers | 1 | 1 | 361 | 4518.5164
1550-Flue gas recirculation fan motors | 1 | 1 | 138 | 2152.8
1560-Other flue gas recirculation fan problems | 1 | 1 | 95.9 | 75.1216
1570-Flue gas recirculation ducts | 3 | 3 | 947 | 14629.2161
1572-Flue gas recirculation duct expansion joints | 9 | 5 | 455 | 44295.7664
1580-Flue gas recirculation dampers | 3 | 3 | 563 | 5992.0165
1591-Stack damper and linkage | 2 | 2 | 502.5 | 675.6248
1599-Other miscellaneous boiler air and gas system problems | 132 | 132 | 9650.39 | 657611.9705
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 157 | 157 | 36768.21 | 197676.3092
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 120 | 107 | 12247 | 99912.5634
1720-Desuperheater/attemperator controls | 54 | 54 | 13300.97 | 100187.0801
1730-Boiler explosion or implosion | 1 | 1 | 249 | 41.4998
1740-Boiler drum gage glasses/level indicator | 85 | 85 | 19813.11 | 104716.895
1750-Burner management system | 156 | 154 | 31743.36 | 439804.0676
1760-Feedwater instrumentation (not local controls) | 22 | 22 | 3026 | 8140.3268
1761-Combustion /Steam condition instrumentation (not local controls) | 13 | 13 | 4123.3 | 28350.4652
1762-Desuperheater/attemperator instrumentation (not local controls) | 13 | 13 | 3197 | 85056.3658
1799-Other boiler instrumentation and control problems | 177 | 177 | 38434.51 | 407577.3785
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 8 | 8 | 138 | 18576.5
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 54 | 54 | 1637.9 | 140315.3663
1810-Other boiler inspections | 3 | 3 | 253 | 6074.2165
1811-Boiler Inspections - problem identification/investigative | 7 | 6 | 961.05 | 24527.1449
1812-Boiler Inspections - scheduled or routine | 14 | 14 | 1196.69 | 479163.1548
1850-Boiler water condition (not feedwater water quality) | 175 | 173 | 25679.73 | 490234.2245
1900-Improper balance between tube sections not due to fouling or plugging | 2 | 2 | 287 | 893.9166
1910-Inadequate air not due to equipment problems | 34 | 34 | 563.19 | 247794.2031
1980-Boiler safety valve test | 4 | 4 | 204 | 434.8333
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 21 | 21 | 4565.29 | 23865.6221
1999-Boiler; miscellaneous | 563 | 466 | 30189.48 | 1140979.6857
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 18 | 18 | 1794.42 | 70053.0014
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 32 | 31 | 1792.04 | 28857.3407
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 3 | 3 | 370.53 | 9700.8415
2031-Fuel preconditioning | 1 | 1 | 10.32 | 18.576
2035-Core xenon restrictions | 5 | 5 | 67 | 964.8
2037-Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | 2 | 2 | 1386.31 | 23141.7333
2040-Core physics tests | 2 | 2 | 1202.41 | 62597.9446
2060-Excore nuclear instrumentation | 2 | 2 | 747.94 | 2154.756
2061-Incore nuclear instrumentation | 1 | 1 | 521 | 51136.15
2070-Normal refueling | 5 | 5 | 5255.6 | 1064739.5719
2071-Refueling equipment problems | 1 | 1 | 1176 | 49313.5996
2090-Other core/fuel problems | 1 | 1 | 837 | 24175.3497
2110-Control rod drive motors | 1 | 1 | 1176 | 62759.1992
2112-Control rod hydraulic drives | 2 | 2 | 313.64 | 2515.7692
2120-Control rod scram mechanisms | 2 | 2 | 1410.39 | 63585.776
2140-Control rod drive cooling | 1 | 1 | 186.76 | 712.8005
2150-Control rod instrumentation | 1 | 1 | 43 | 1595.3
2151-Control rod drive controls | 3 | 3 | 2499 | 219787.5663
2155-Control rod testing | 2 | 2 | 1128 | 73562.5996
2160-Other control rod drive problems | 2 | 2 | 296.89 | 27067.1885
2200-Reactor coolant/recirculating pumps | 10 | 10 | 4193.54 | 299209.1465
2210-Reactor coolant/recirculating pump motors | 6 | 6 | 4048 | 295931.0819
2220-Reactor coolant/recirculating pump MG sets | 1 | 1 | 301.31 | 1029.4756
2230-Reactor coolant system piping | 5 | 5 | 2288.5 | 155370.6704
2260-Reactor coolant flanges; fittings; and manways | 3 | 3 | 2171 | 295032.9162
2290-Pressurizer spray valves | 2 | 2 | 1864 | 114752.5
2300-Recirculation loop flow control valves | 1 | 1 | 24.49 | 68.572
2350-BWR feedwater controls | 2 | 2 | 511.72 | 20465.8925
2390-Other reactor coolant system instruments and controls | 1 | 1 | 736.08 | 25750.5318
2400-Steam generator tube leaks | 5 | 5 | 4278.23 | 863304.6416
2411-Steam generator tube inspections | 1 | 1 | 171.4 | 40881.7566
2421-Steam generator feedwater nozzles | 1 | 1 | 28.1 | 15309.3483
2422-Other steam generator internals problems | 1 | 1 | 7.32 | 5446.08
2440-Steam generator chemistry (excluding feedwater chemistry) | 55 | 55 | 706.96 | 49335.4821
2480-Other blowdown | 1 | 1 | 726.6 | 19448.6595
2510-Main steam isolation valves (BWR and PWR) | 3 | 3 | 3098.12 | 155683.9859
2520-Main steam safety/relief valves (except BWR) | 1 | 1 | 938 | 67551.6327
2530-Atmospheric or condenser dump valves (not SRVs) | 9 | 8 | 72 | 52440
2540-Other steam valves | 2 | 2 | 532.8 | 11836.1663
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 1 | 1 | 837 | 33619.4994
2599-Other steam generator problems | 2 | 2 | 93.34 | 3007.1037
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 2 | 2 | 1759.4 | 112125.4022
2602-Steam turbine drives for high pressure pumps (including RCIC) | 1 | 1 | 7.3 | 3.0417
2603-High pressure piping | 3 | 3 | 1867 | 204503.9162
2604-High pressure valves | 1 | 1 | 1158 | 113754.1996
2740-Containment penetration pressurization system | 1 | 1 | 1174.8 | 48049.32
2770-Containment cooling system - normal | 1 | 1 | 203.49 | 39432.9704
2817-Instruments and controls | 1 | 1 | 47.8 | 361.6866
2830-Nuclear service water pumps | 1 | 1 | 241.02 | 257.0878
2890-Condenser off-gas system problems | 1 | 1 | 45 | 2160
3110-Condenser tube leaks | 136 | 136 | 31044.08 | 1234280.9228
3111-Condenser tube fouling shell side | 6 | 6 | 502 | 8414.8332
3112-Condenser tube fouling tube side | 237 | 226 | 20598.26 | 296108.011
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 74 | 73 | 7876.47 | 132632.1203
3114-Air-cooled condenser tubes | 2 | 2 | 91 | 1856.3666
3115-Air-cooled condenser pumps | 2 | 2 | 705.5 | 1238.4415
3116-Air-cooled condenser fans | 10 | 9 | 404.8 | 4363.5898
3117-Air-cooled condenser fan motors | 2 | 2 | 213 | 177.4999
3118-Other Air-cooled condenser problems | 192 | 184 | 4748.82 | 11572.9449
3119-Other condenser tube casing or shell and internal problems | 4 | 4 | 1112.21 | 9010.5261
3120-Tube sheets | 4 | 4 | 2396.49 | 457452.7463
3121-Expansion joint | 18 | 18 | 1416.85 | 58399.6459
3122-Gaskets and seals | 8 | 8 | 1386.92 | 26020.963
3123-Hot well | 12 | 12 | 1730 | 9109.2075
3124-Tube sheet fouling | 11 | 11 | 2527 | 7345.8324
3129-Other condenser casing or shell and internal problems | 4 | 4 | 945 | 90187.8161
3130-Air ejectors | 14 | 14 | 1867.75 | 28385.9833
3131-Air ejector piping and valves | 7 | 7 | 1271.47 | 58169.3484
3132-Inter and after condensers | 3 | 3 | 164 | 12251.2999
3133-Vacuum pumps | 31 | 31 | 6494.77 | 42572.59
3134-Vacuum pump piping and valves | 3 | 3 | 737.39 | 60110.04
3135-Vacuum pump motor and auxiliaries | 8 | 8 | 1794.25 | 12022.5037
3139-Other air extraction system problems - general | 19 | 19 | 4236.5 | 112637.8487
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 140 | 140 | 26728.16 | 497508.3666
3150-Hot well level controls | 25 | 25 | 3493.3 | 36948.2654
3151-Vacuum pump and air ejector controls | 3 | 3 | 284.61 | 338.6777
3152-Air-cooled condenser controls | 2 | 2 | 379.25 | 101.1331
3159-Other condensing system controls and instruments | 14 | 14 | 3076 | 89939.5997
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 3 | 3 | 641 | 7527.1833
3180-Major condenser overhaul | 1 | 1 | 10 | 75.6667
3186-Auxiliary Condenser and Associated Equipment | 38 | 38 | 1913.68 | 25982.3662
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 36 | 36 | 4886.17 | 456383.0024
3199-Other miscellaneous condensing system problems | 75 | 75 | 9607.88 | 124476.9217
3210-Circulating water pumps | 226 | 225 | 24131.6 | 2183395.4366
3211-Circulating water pump motors | 142 | 142 | 13980.61 | 697976.4719
3220-Circulating water piping | 43 | 43 | 8980.4 | 619883.7874
3221-Circulating water piping fouling | 6 | 6 | 986 | 75650.8497
3230-Circulating water valves | 60 | 60 | 7012.01 | 180431.3152
3231-Waterbox | 6 | 6 | 1125.2 | 73357.7795
3232-Condenser tube cleaning system including debris filter | 30 | 30 | 8947 | 28404.7125
3233-Circulating water priming system | 4 | 4 | 1514.9 | 22586.4232
3235-Cooling tower booster pump | 6 | 6 | 468.4 | 84099.0732
3238-Cooling tower fan motors | 12 | 12 | 876.97 | 45843.3664
3239-Cooling tower fan motors - variable speed | 1 | 1 | 36 | 1125.6
3240-Cooling tower fans | 55 | 54 | 4117.04 | 210507.7533
3241-Cooling tower efficiency below design | 32 | 32 | 1326.08 | 17464.6143
3242-Cooling tower fill damage | 22 | 22 | 1318.9 | 83727.0829
3245-Other cooling tower problems | 54 | 54 | 4617.59 | 903564.209
3246-Cooling tower fouling | 5 | 5 | 146 | 22354.5833
3247-Cooling tower instrumentation | 5 | 5 | 831 | 1457.2162
3250-Circulating water system instruments and controls | 12 | 12 | 3308.63 | 20194.6406
3260-Traveling screens | 26 | 26 | 4473.1 | 215346.9017
3261-Traveling screen fouling | 24 | 24 | 1729.91 | 16810.3848
3269-Circulating water biological conditions (ie; zebra mussels) | 2 | 2 | 314 | 667.2498
3270-Intake system problems other than traveling screens | 22 | 22 | 4362 | 263666.7651
3271-Intake grating fouling | 17 | 17 | 1680.9 | 11581.0748
3272-Circulating water screenwash system | 6 | 6 | 2242 | 704190.4158
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 21 | 21 | 2075.26 | 30305.6487
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 2 | 2 | 1130 | 63622.833
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 70 | 65 | 4650.15 | 129733.9117
3281-Circulating water tempering system | 4 | 4 | 297.5 | 5466.8666
3285-Circulating water chemistry | 41 | 39 | 4368.25 | 88178.3324
3292-Waste water (zero discharge) piping | 1 | 1 | 23 | 499.4833
3295-Other Waste water (zero discharge) problems | 110 | 14 | 64 | 450.25
3299-Other circulating water system problems | 120 | 118 | 14226.47 | 374238.0722
3300-Condensate water pre-treatment | 6 | 6 | 959 | 40270.8563
3310-Condensate/hotwell pumps | 79 | 79 | 10466.65 | 607873.6759
3311-Condensate/hotwell pump motor | 39 | 39 | 7541.63 | 429426.7263
3312-Condensate booster pump | 14 | 14 | 3464.56 | 40249.0884
3313-Condensate booster pump motor | 6 | 6 | 1125 | 14859.933
3315-Condensate booster pump drive (other than 3313 and 3314) | 1 | 1 | 166.81 | 1584.695
3320-Condensate piping | 9 | 9 | 1663.8 | 22966.491
3330-Condensate valves | 37 | 37 | 9675.01 | 228393.2846
3339-LP heater head leaks | 1 | 1 | 99.5 | 402.975
3340-LP heater tube leaks | 14 | 14 | 1356 | 72468.8329
3341-Other LP heater - general | 13 | 13 | 2135.99 | 57450.3095
3342-IP heater tube leaks | 3 | 3 | 1750 | 74636.3328
3343-Other IP heater - general | 6 | 6 | 605.51 | 49500.482
3344-Deaerator (including level control) | 49 | 49 | 11531.62 | 411675.1439
3350-Condensate polishing and filtering systems | 55 | 55 | 8964.53 | 259813.291
3351-Chemical addition systems | 11 | 11 | 2557.06 | 31395.1835
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 87 | 87 | 16189.05 | 538201.9731
3360-Condensate makeup and return (including storage tanks) | 23 | 23 | 3646.53 | 63187.7955
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 17 | 17 | 3172.02 | 16062.8491
3380-Condensate coolers | 1 | 1 | 471 | 808.5497
3399-Other miscellaneous condensate system problems | 28 | 28 | 6239.06 | 72424.7809
3401-Startup feedwater pump | 18 | 18 | 6484.09 | 527014.4771
3402-Startup feedwater pump drives - all types | 7 | 7 | 2024.62 | 10454.8828
3407-Feedwater pump suction screens | 11 | 11 | 1735.2 | 17052.7594
3408-Feedwater pump drive - local controls | 38 | 38 | 12402.17 | 481725.7167
3409-Feedwater pump drive motor - variable speed | 3 | 3 | 578 | 15845.2496
3410-Feedwater pump | 371 | 366 | 63067.14 | 3745088.4015
3411-Feedwater pump drive - motor | 86 | 86 | 13775.63 | 1425857.1471
3412-Feedwater pump drive - steam turbine | 128 | 128 | 35861.16 | 2562850.1383
3413-Feedwater pump coupling and drive shaft | 17 | 17 | 4972.2 | 392412.342
3414-Feedwater pump local controls | 45 | 45 | 9567.37 | 77624.3296
3415-Feedwater pump/drive lube oil system | 74 | 73 | 18032.74 | 410803.3601
3416-Other feedwater pump problems | 102 | 102 | 27543.74 | 1165662.8491
3417-Feedwater pump drive - main shaft | 6 | 6 | 261 | 5053.8999
3418-Feedwater pump drive - other | 21 | 19 | 3737 | 92710.5149
3419-Feedwater pump drive - gear | 2 | 2 | 368.32 | 13823.0265
3420-Feedwater piping and supports | 26 | 26 | 7324.99 | 336378.2483
3430-Feedwater regulating (boiler level control) valve | 126 | 125 | 29699.31 | 719765.9967
3431-Other feedwater valves | 138 | 138 | 31875.5 | 1231525.3084
3439-HP heater head leaks | 18 | 18 | 2764.2 | 130198.4659
3440-High pressure heater tube leaks | 93 | 93 | 11774.17 | 834134.2892
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 75 | 75 | 8332.73 | 158020.116
3451-Feedwater Booster Pump Suction Screens | 1 | 1 | 382.5 | 4035.375
3454-Feedwater Booster Pump | 7 | 7 | 2809.4 | 71461.5425
3456-Feedwater Booster Pump Drive - Steam Turbine | 1 | 1 | 244 | 1785.2665
3458-Feedwater Booster Pump Local Controls | 3 | 3 | 355.7 | 1370.7265
3459-Feedwater Booster Pump/Drive Lube Oil System | 3 | 3 | 605.9 | 6034.0765
3460-Other Feedwater Booster Pump Problems | 4 | 4 | 570 | 964.4165
3499-Other feedwater system problems | 97 | 97 | 19513.97 | 653872.1874
3501-Heater drain pumps | 54 | 54 | 4786.57 | 140259.2494
3502-Heater level control | 33 | 33 | 2601.4 | 120582.7603
3503-Heater drain piping | 5 | 5 | 999 | 75066.9997
3504-Heater drain valves | 27 | 27 | 2418 | 39077.9053
3505-Heater drain pump drive | 4 | 4 | 251 | 7132.0833
3509-Other heater drain system problems | 6 | 6 | 364.6 | 6663.7365
3520-HP Extraction steam piping | 3 | 3 | 508.2 | 118362.6597
3521-HP Extraction steam valves | 12 | 12 | 2590.2 | 48948.4989
3522-HP Extraction steam instruments and controls | 3 | 3 | 443.89 | 1368.9044
3529-Other HP extraction steam system problems | 4 | 4 | 1046.4 | 38187.1931
3530-IP Extraction steam piping | 2 | 2 | 1149 | 73966.8328
3531-IP Extraction steam valves | 2 | 2 | 641 | 12357.1498
3532-IP Extraction steam instruments and controls | 1 | 1 | 228 | 18.9999
3539-Other IP extraction steam system problems | 1 | 1 | 71 | 6425.5
3541-LP Extraction steam valves | 2 | 2 | 679 | 99251.8333
3542-LP Extraction steam instruments and controls | 1 | 1 | 347.18 | 8355.4651
3549-Other LP extraction steam system problems | 4 | 4 | 1330 | 1625.5828
3600-Switchyard transformers and associated cooling systems - external | 44 | 44 | 4460.96 | 134704.2131
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 7 | 7 | 1056.14 | 12431.9831
3610-Switchyard circuit breakers - (not outside management control) | 50 | 50 | 8523.32 | 675475.151
3611-Switchyard circuit breakers - external | 100 | 100 | 18255.88 | 1347351.1875
3612-Switchyard system protection devices - external | 102 | 102 | 12637.25 | 263964.5463
3613-Switchyard system protection devices - (not outside management control) | 39 | 39 | 6557.43 | 2417976.3955
3618-Other switchyard equipment ? (not outside management control) | 51 | 51 | 6705.26 | 147439.3463
3619-Other switchyard equipment - external | 95 | 92 | 17926.38 | 620601.8969
3620-Main transformer | 276 | 274 | 37343.86 | 10726908.4421
3621-Unit auxiliaries transformer | 105 | 105 | 21369.5 | 1359087.1024
3622-Station service startup transformer | 43 | 43 | 9743.47 | 204418.3796
3623-Auxiliary generators | 3 | 3 | 1337.32 | 218037.8764
3624-Generator Voltage Supply System | 13 | 13 | 866.5 | 78827.5495
3629-Other switchyard or high voltage system problems - external | 71 | 70 | 8808.44 | 193616.2392
3630-480-volt transformers | 17 | 17 | 2848.28 | 29781.22
3631-480-volt circuit breakers | 69 | 69 | 9107.1 | 51030.2963
3632-480-volt conductors and buses | 51 | 51 | 6282.65 | 194775.1675
3634-480-volt protection devices | 10 | 10 | 1881.12 | 12184.5107
3639-Other 480-volt problems | 24 | 24 | 3883.04 | 140858.7387
3640-AC instrument power transformers | 9 | 9 | 907.9 | 32010.8447
3641-AC Circuit breakers | 60 | 60 | 10461.62 | 318748.8914
3642-AC Conductors and buses | 13 | 13 | 3467.1 | 148013.9433
3643-AC Inverters | 15 | 15 | 4543.32 | 71310.4572
3644-AC Protection devices | 137 | 134 | 15121.33 | 223500.7537
3649-Other AC instrument power problems | 17 | 17 | 2504.88 | 62407.5917
3650-DC instrument power battery chargers | 23 | 23 | 1820.17 | 1468228.8341
3651-DC circuit breakers | 10 | 10 | 735 | 12417.983
3652-DC conductors and buses | 3 | 3 | 399 | 17128.4999
3653-DC protection devices | 41 | 41 | 3404.65 | 157233.6513
3659-Other DC power problems | 44 | 44 | 4331.4 | 404078.6374
3660-4160-volt transformers | 13 | 13 | 2732.5 | 66485.8822
3661-4160-volt circuit breakers | 94 | 94 | 21030.64 | 307832.5023
3662-4160-volt conductors and buses | 32 | 32 | 8908.81 | 630350.4941
3664-4160-volt protection devices | 19 | 19 | 3389.64 | 46670.5407
3669-Other 4160-volt problems | 16 | 16 | 1700.6 | 13027.366
3670-12kV transformers | 11 | 11 | 1841.9 | 79540.0942
3671-12kV circuit breakers | 56 | 56 | 4713.34 | 545269.0253
3672-12kV conductors and buses | 17 | 17 | 1081.38 | 81092.0335
3673-12kV insulators | 6 | 6 | 539.94 | 22144.3299
3674-12kV protection devices | 33 | 33 | 3979.28 | 384785.7852
3679-Other 12kV problems | 4 | 4 | 382 | 54485.0498
3680-Other voltage system transformers | 14 | 14 | 2204.64 | 755781.2337
3681-Other voltage system breakers | 45 | 44 | 7219 | 196839.947
3682-Other voltage system conductors and buses | 14 | 14 | 1806.19 | 77252.828
3683-Other voltage system insulators | 8 | 8 | 223.5 | 4661.725
3684-Other voltage system protection devices | 31 | 30 | 4756.34 | 247021.685
3689-Other Other voltage system problems | 42 | 42 | 8234.99 | 532172.6666
3690-Station Service Power Distribution System; General | 66 | 65 | 8886.26 | 246886.2001
3700-Power Station switchyard (non generating unit equipment) | 42 | 42 | 5261.31 | 223780.6501
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 92 | 92 | 8256.44 | 463635.4406
3720-Transmission equipment at the 1st substation) | 63 | 63 | 9574.31 | 194482.3224
3730-Transmission equipment beyond the 1st substation | 84 | 84 | 10776.25 | 260499.0135
3800-Open cooling water pumps and motors | 4 | 4 | 312.7 | 1192.2549
3801-Open cooling water piping | 3 | 3 | 340.8 | 15005.9165
3802-Open cooling water valves | 1 | 1 | 45 | 70.5
3803-Open cooling water heat exchangers | 1 | 1 | 295 | 1416
3804-Open cooling water system fouling | 2 | 2 | 354.7 | 989.9664
3805-Open cooling water system instrumentation | 1 | 1 | 393 | 222.6997
3809-Other open cooling water problems | 4 | 4 | 370 | 62737.6333
3810-Service water pumps and motors | 19 | 19 | 1061.28 | 19585.5569
3811-Service water piping | 13 | 13 | 909.97 | 8138.8267
3812-Service water valves | 9 | 8 | 417.99 | 5374.6025
3813-Service water heat exchangers | 8 | 8 | 613 | 28231.0666
3814-Service water system fouling | 15 | 15 | 1793.05 | 43565.6681
3819-Other service water problems A | 22 | 22 | 3525.25 | 218420.0983
3820-Closed cooling water pumps | 17 | 17 | 2423.65 | 24681.9168
3821-Closed cooling water piping | 16 | 16 | 2075.18 | 88783.6818
3822-Closed cooling water valves | 6 | 6 | 442 | 786.0166
3823-Closed cooling water heat exchangers | 23 | 23 | 2725.85 | 175384.707
3824-Closed cooling water system fouling | 24 | 19 | 4791 | 26284.4491
3825-Closed cooling water instrumentation | 1 | 1 | 233 | 287.3666
3829-Other closed cooling water system problems A | 31 | 31 | 2657.86 | 8602.8267
3830-Auxiliary boiler | 34 | 34 | 8286.45 | 92097.0394
3831-Auxiliary steam piping | 7 | 7 | 1012.9 | 42844.2331
3832-Auxiliary steam valves | 11 | 11 | 2465.75 | 151866.8702
3833-Auxiliary steam controls and instruments | 18 | 18 | 4684.1 | 24677.6865
3834-Auxiliary boiler tube leaks | 6 | 6 | 1251.9 | 89324.9331
3835-Auxiliary boiler burner management system | 3 | 3 | 727 | 1818
3836-Steam Transfer to Other Unit | 61 | 61 | 7479.37 | 96376.7203
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 9 | 9 | 3789.06 | 71038.0128
3840-Service air compressors | 18 | 18 | 3390 | 6459.5568
3841-Service air piping | 2 | 2 | 590 | 650.6665
3842-Service air valves | 2 | 2 | 30 | 129.8
3843-Service air dryers | 1 | 1 | 86 | 394.1666
3844-Soot blowing air compressor and system | 7 | 7 | 1384 | 92062.4493
3849-Other service air problems | 13 | 13 | 1468.32 | 12011.7071
3850-Instrument air compressors | 49 | 49 | 6473.1 | 55806.3291
3851-Instrument air piping | 14 | 14 | 2932.92 | 24077.9241
3852-Instrument air valves | 12 | 12 | 1158.1 | 25476.2628
3853-Instrument air dryers | 8 | 8 | 1295 | 62122.0661
3859-Other instrument air problems | 8 | 8 | 1653.15 | 15131.9998
3860-Fire protection system pumps | 5 | 5 | 246.7 | 932.3
3861-Fire protection system piping | 7 | 7 | 705.9 | 181523.775
3862-Fire protection system valves | 1 | 1 | 216 | 648
3864-Fire protection system instrumentation and controls | 65 | 65 | 5885.19 | 136093.9709
3869-Other fire protection system problems | 58 | 58 | 4569.96 | 188000.4519
3870-Fuel Gas Compressor and Motors | 28 | 28 | 1076.02 | 17089.0897
3871-Fuel Gas Compressor Piping | 26 | 26 | 2403.2 | 52958.7061
3872-Fuel Gas Compressor Valves | 43 | 43 | 3643.21 | 24810.3355
3873-Fuel Gas Compressor Heat Exchangers | 5 | 5 | 707.7 | 2704.5297
3874-Fuel Gas Compressor Controls and Instrumentation | 67 | 67 | 3472.84 | 14675.7256
3876-Fuel Gas Compressor Fire System | 2 | 2 | 474 | 533.25
3879-Fuel Gas Compressor - other | 70 | 70 | 2322.88 | 8377.9764
3880-Seal air fan | 1 | 1 | 96 | 8544
3882-Seal air control dampers and drives | 1 | 1 | 42 | 42
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 63 | 63 | 5189.86 | 65721.7871
3899-Other miscellaneous auxiliary system problems | 129 | 129 | 13148.09 | 464376.3235
3950-Process computer | 50 | 50 | 4095.99 | 24500.8417
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 115 | 111 | 2509.32 | 390896.4163
3970-Distributive Control System (DCS) - process computer | 37 | 37 | 5222.29 | 149407.1387
3971-DCS - data highway | 84 | 84 | 7279.41 | 1069100.6797
3972-DCS - hardware problems (including card failure) | 151 | 150 | 22745.93 | 293057.8515
3973-DCS - internal and termination wiring | 17 | 17 | 1296.6 | 44225.1461
3974-DCS - logic problems | 46 | 46 | 15691.39 | 251334.252
3975-DCS - upgrades | 12 | 12 | 1504.99 | 31571.3679
3979-Other DCS problems | 81 | 81 | 9863.3 | 81739.97
3980-Programmable Logic Controller (PLC) | 32 | 32 | 2088.22 | 21915.1228
3981-PLC - data highway | 32 | 32 | 941.28 | 9570.1493
3982-PLC - hardware problems (including card failure) | 33 | 33 | 3733.18 | 55429.3584
3983-PLC - internal and termination wiring | 9 | 9 | 487.5 | 3788.7915
3984-PLC - logic problems | 19 | 19 | 1835.67 | 8808.263
3985-PLC - upgrades | 11 | 11 | 868 | 12610.9663
3989-Other PLC problems | 33 | 33 | 2358.75 | 10307.572
3995-Powerhouse heating and ventilating systems | 2 | 2 | 76.98 | 375.0709
3996-Air conditioning systems - rooms and areas | 10 | 10 | 2191 | 19001.5497
3998-Balance of plant overhaul/outage | 30 | 29 | 3374.99 | 365340.5947
3999-Other miscellaneous balance of plant problems | 815 | 786 | 76228.25 | 2192952.4431
4000-Outer casing A | 4 | 4 | 702 | 36397.0332
4001-Inner casing C | 1 | 1 | 415 | 74333.4164
4009-Nozzle bolting A | 2 | 2 | 44 | 1170.6
4010-Nozzles and nozzle blocks C | 6 | 6 | 1999.98 | 1220987.79
4011-Diaphragms A | 1 | 1 | 258 | 1526.4998
4012-Buckets or blades A | 3 | 3 | 220 | 31511.5833
4013-Diaphragms unit and shroud type | 2 | 2 | 338 | 221944.8833
4014-Bucket or blade fouling C | 59 | 48 | 519 | 140203.7332
4020-Shaft seals B | 3 | 3 | 1198.8 | 5294.3396
4030-Rotor shaft C | 16 | 15 | 2563.4 | 311954.3956
4040-Bearings C | 59 | 59 | 14651.81 | 3179719.8937
4041-HP steam turbine thrust bearings | 13 | 13 | 2801.5 | 720110.4158
4099-Other high pressure turbine problems | 56 | 56 | 13499.85 | 3126925.7813
4112-Buckets or blades B | 1 | 1 | 554 | 283334.0665
4130-Rotor shaft B | 2 | 2 | 502 | 4150.2999
4140-Bearings D | 17 | 17 | 3937 | 10493.682
4141-IP steam turbine thrust bearings | 14 | 14 | 3156.84 | 193799.4469
4199-Other intermediate pressure turbine problems | 25 | 25 | 5508.09 | 647161.9301
4201-Inner casing A | 1 | 1 | 243 | 526.4998
4211-Diaphragms C | 10 | 10 | 3218.6 | 47355.8951
4212-Buckets or blades C | 56 | 56 | 5864.47 | 2508417.1936
4220-Shaft seals D | 2 | 2 | 46.2 | 12590.33
4222-Gland rings A | 2 | 2 | 215 | 144757.6665
4230-Rotor shaft A | 3 | 3 | 1465 | 464364.8332
4240-Bearings E | 39 | 39 | 8145.5 | 229964.906
4250-Other low pressure turbine problems | 46 | 46 | 11218.6 | 999171.7987
4260-Main stop valves | 99 | 99 | 20267.78 | 1026981.1756
4261-Control valves | 249 | 248 | 57737.97 | 3032220.5258
4262-Intercept valves | 52 | 52 | 12277.39 | 236485.6182
4263-Reheat stop valves | 32 | 32 | 13045.42 | 287967.8307
4264-Combined intercept valves | 3 | 3 | 740 | 14872.6998
4265-Miscellaneous drain and vent valves | 27 | 27 | 6132.42 | 230490.8025
4266-Main stop valve testing | 13 | 13 | 1643.66 | 4020.8817
4267-Control valve testing | 35 | 35 | 7157.41 | 131149.3445
4268-Reheat/intercept valve testing | 21 | 21 | 5699.64 | 157424.8127
4269-Other turbine valves (including LP steam admission valves) | 93 | 93 | 22502.69 | 372961.3896
4270-Crossover or under piping | 10 | 10 | 3091 | 77963.6994
4279-Miscellaneous turbine piping | 38 | 38 | 14514.37 | 623822.0845
4280-Lube oil pumps A | 36 | 36 | 7938.41 | 667736.1286
4281-Lube oil coolers A | 17 | 17 | 3209.28 | 114085.7752
4283-Lube oil system valves and piping | 19 | 19 | 3237.89 | 3932058.8812
4284-Lube oil pump drive | 4 | 4 | 943 | 127703.5
4289-Other lube oil system problems | 90 | 89 | 12075.69 | 506236.9939
4290-Hydraulic system pumps | 21 | 21 | 6085.67 | 146936.3756
4291-Hydraulic system coolers | 1 | 1 | 113 | 2433.2666
4292-Hydraulic system filters | 3 | 3 | 1371 | 8746.9833
4293-Hydraulic system pipes and valves | 94 | 93 | 30230.75 | 3282045.8866
4299-Other hydraulic system problems | 74 | 74 | 22414.21 | 1579596.7671
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 25 | 25 | 6665.6 | 87439.3571
4301-Turbine governing system | 69 | 69 | 12498.88 | 321596.2482
4302-Turbine trip devices (including instruments) | 161 | 160 | 30385.53 | 289129.3434
4303-Exhaust hood and spray controls | 14 | 14 | 2891.86 | 36512.2314
4304-Automatic turbine control systems - mechanical | 6 | 6 | 1154.8 | 28234.0129
4305-Automatic turbine control systems - mechanical - hydraulic | 21 | 21 | 2515.2 | 183288.3259
4306-Automatic turbine control systems - electro-hydraulic - analog | 7 | 7 | 1552 | 8005.8658
4307-Automatic turbine control systems - electro-hydraulic - digital | 21 | 21 | 6321.55 | 327410.2027
4308-Automatic turbine control systems - digital control and monitoring | 40 | 40 | 8681.65 | 147863.5905
4309-Other turbine instrument and control problems | 96 | 96 | 20761.65 | 601642.2372
4310-Steam Turbine Control System - data highway | 10 | 10 | 1484.4 | 58828.1733
4311-Steam Turbine Control System - hardware problems (including card failure) | 70 | 70 | 14928.47 | 176000.8167
4312-Steam Turbine Control System - internal and termination wiring | 13 | 13 | 2600.2 | 75943.9188
4313-Steam Turbine Control System - logic problems | 49 | 49 | 8232.5 | 265439.8847
4314-Steam Turbine Control System - upgrades | 3 | 3 | 206.7 | 678.5466
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 21 | 21 | 4674.4 | 1773124.1679
4401-Inspection F | 4 | 4 | 690.64 | 37364.5897
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 1 | 1 | 27 | 2153.7
4410-Turning gear and motor A | 47 | 47 | 11778.7 | 831781.4708
4411-Steam turbine gear box (single shaft configuration) | 3 | 3 | 108.26 | 42278.606
4412-Steam turbine clutch (single shaft configuration) | 11 | 11 | 2793.46 | 6494.9939
4415-Shaft coupling mechanism | 3 | 3 | 476 | 160930.2999
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 190 | 189 | 36218.08 | 4585815.9882
4430-Gland seal system | 58 | 58 | 14782.75 | 503187.9159
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 5 | 5 | 577.06 | 17960.2397
4445-Steam reheater | 1 | 1 | 36 | 378
4450-Water induction | 4 | 4 | 868 | 2242.3996
4460-Turbine overspeed trip test | 4 | 4 | 479 | 1066.4667
4470-Differential expansion | 75 | 75 | 22696.36 | 226511.7554
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 3 | 3 | 65 | 1044.2667
4499-Other miscellaneous steam turbine problems | 242 | 239 | 42496.93 | 2383965.41
4500-Rotor windings (including damper windings and fan blades on hydro units) | 120 | 120 | 9368.23 | 3401037.2216
4510-Rotor collector rings | 4 | 4 | 281 | 12360.9498
4511-Rotor; General | 21 | 21 | 4764.3 | 4082785.5561
4520-Stator windings; bushings; and terminals | 36 | 36 | 4907.04 | 5334267.1732
4530-Stator core iron | 4 | 4 | 321.8 | 381533.435
4535-Stator; General | 73 | 73 | 9446.97 | 2166440.6354
4536-Generator heaters | 2 | 2 | 58.2 | 79.4833
4540-Brushes and brush rigging | 20 | 20 | 3054.37 | 300058.2381
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 124 | 124 | 9567.3 | 763300.8976
4551-Generator bearings | 85 | 84 | 11290.98 | 1405360.0371
4552-Generator lube oil system | 81 | 80 | 5051.95 | 150744.0452
4555-Bearing cooling system A | 58 | 58 | 4176.91 | 244227.3885
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 119 | 119 | 18815.1 | 1914918.8082
4570-Generator casing | 9 | 9 | 1989.5 | 137966.0242
4580-Generator end bells and bolting | 3 | 3 | 1502 | 18792.4162
4590-Generator brakes | 40 | 40 | 2876.64 | 42638.5139
4600-Exciter drive - motor | 8 | 8 | 799 | 170030.9531
4601-Exciter field rheostat | 8 | 8 | 2140.07 | 38351.6278
4602-Exciter commutator and brushes | 41 | 41 | 4200.22 | 548703.4441
4603-Solid state exciter element | 33 | 33 | 5901.63 | 553123.974
4604-Exciter drive - shaft | 8 | 8 | 479.66 | 212315.0088
4605-Exciter transformer | 25 | 25 | 4353 | 393495.7571
4609-Other exciter problems | 572 | 571 | 77451.79 | 3667936.1787
4610-Hydrogen cooling system piping and valves | 22 | 22 | 4051.49 | 146741.7838
4611-Hydrogen coolers | 44 | 44 | 5818.5 | 407966.8658
4612-Hydrogen storage system | 1 | 1 | 317.22 | 18541.509
4613-Hydrogen seals | 12 | 12 | 3364.75 | 392158.3163
4619-Other hydrogen system problems | 27 | 27 | 7254.48 | 161490.3794
4620-Air cooling system | 56 | 54 | 5706.41 | 102066.9048
4630-Liquid cooling system | 66 | 66 | 15591.87 | 1053699.3914
4640-Seal oil system and seals A | 25 | 25 | 7231.15 | 708608.3123
4650-Other cooling system problems | 70 | 69 | 9758.33 | 778226.5947
4700-Generator voltage control | 184 | 183 | 28464.89 | 1235360.8909
4710-Generator metering devices | 40 | 40 | 7385.66 | 89611.749
4720-Generator synchronization equipment | 153 | 153 | 15223.92 | 139825.158
4730-Generator current and potential transformers | 76 | 76 | 12938.05 | 950495.4512
4740-Emergency generator trip devices | 191 | 188 | 29523.39 | 2963147.7826
4750-Other generator controls and metering problems | 218 | 217 | 28603.84 | 548227.1356
4800-Generator main leads | 20 | 20 | 4476.8 | 2478127.091
4805-Generator Bus Duct Cooling System | 8 | 8 | 2116.05 | 211182.6443
4810-Generator output breaker | 285 | 280 | 28027.89 | 1984124.7348
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 2 | 2 | 133.9 | 2473.7049
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 4 | 4 | 217.5 | 101720.4749
4840-Inspection E | 31 | 30 | 1780.11 | 471780.5407
4841-Generator doble testing | 1 | 1 | 70 | 280
4842-Reactive and capability testing | 4 | 4 | 128.24 | 58615.7273
4850-Core monitor alarm | 2 | 2 | 448 | 64973.0664
4860-Generator Neutral Grounding Equipment | 20 | 20 | 2942.7 | 196478.5603
4899-Other miscellaneous generator problems | 262 | 261 | 34140.99 | 6231714.7171
5000-Inlet air ducts A | 12 | 12 | 1710.2 | 6572.8162
5001-Inlet air vanes / nozzles | 123 | 122 | 12825.08 | 471847.526
5002-Inlet air filters A | 120 | 120 | 8823.99 | 241738.5831
5004-Inlet air chillers B | 66 | 58 | 1629.54 | 33013.9499
5005-Inlet air evaporative coolers B | 59 | 55 | 1421.89 | 19310.3928
5006-Inlet air foggers B | 9 | 9 | 215.6 | 10895.7666
5009-Other inlet air problems A | 85 | 85 | 5419.11 | 69209.6097
5010-High pressure shaft D | 2 | 2 | 243.5 | 18793.6333
5011-High pressure bearings C | 3 | 3 | 362.5 | 41726.0916
5012-High pressure blades/buckets B | 17 | 17 | 3109.9 | 1436495.5506
5013-Compressor casing and bolts | 1 | 1 | 100 | 4975
5014-Compressor diaphragms | 3 | 3 | 262.4 | 163555.8399
5015-Compressor seals | 1 | 1 | 166.2 | 3274.14
5016-High pressure compressor bleed valves | 134 | 134 | 20508.64 | 301346.0273
5017-Low pressure compressor bleed valves | 48 | 48 | 6585.06 | 39737.8994
5019-Other high pressure problems A | 7 | 7 | 764.5 | 21578.4415
5021-Low pressure bearings D | 3 | 3 | 348.5 | 50606.9916
5022-Low pressure blades/buckets A | 11 | 11 | 343.28 | 488541.0938
5029-Other low pressure problems E | 5 | 5 | 387 | 3466.8499
5030-Supercharging fans A | 2 | 2 | 123 | 208.7666
5035-Compressor Washing | 19 | 19 | 1269.05 | 89381.5864
5036-Compressor shaft & bearings two sft machines | 1 | 1 | 93 | 294.4999
5037-Inlet bleed heat valve | 82 | 82 | 10794.71 | 79527.101
5039-Other compressor problems | 76 | 76 | 11613.99 | 1390980.9669
5040-Fuel tanks B | 5 | 5 | 482 | 657.0497
5041-Fuel piping and valves A | 612 | 600 | 78904.57 | 1457652.372
5042-Fuel nozzles/vanes B | 61 | 60 | 7660.08 | 460976.5713
5043-Fuel filters A | 62 | 61 | 10680.23 | 218888.1754
5044-Liquid fuel oil pump A | 10 | 10 | 579.4 | 5977.6398
5046-Liquid fuel oil transfer/forwarding pump B | 8 | 8 | 835.6 | 994.1231
5047-Liquid fuel purge system A | 24 | 23 | 3666.7 | 81592.1465
5048-Gas fuel system B | 559 | 556 | 67177.23 | 637785.5064
5049-Other fuel system problems B | 332 | 316 | 37285.89 | 509414.4323
5050-Ignition system A | 256 | 251 | 34801.36 | 240895.2775
5051-Pilot fuel piping and valves A | 110 | 100 | 12387.03 | 147289.8692
5052-Pilot fuel nozzles/vanes B | 2 | 2 | 283 | 839.9832
5053-Pilot fuel filters A | 2 | 2 | 600 | 1264.9998
5054-Water Injection System (Gas Turbine) | 143 | 141 | 8660.05 | 126049.2875
5060-Atomizing air system B | 23 | 23 | 2314.9 | 67425.7127
5065-NOx water injection system including pumps | 71 | 70 | 4082.83 | 83801.3537
5066-NOx Steam Injection System | 14 | 14 | 1173.45 | 9009.5029
5070-Combustor casing A | 13 | 13 | 2221.6 | 110463.661
5071-Combustor liner B | 6 | 6 | 613.5 | 51839.6915
5072-Combustor caps B | 9 | 9 | 1460.4 | 9394.8504
5073-Flame scanners B | 100 | 100 | 12162.11 | 64171.4732
5074-Flashback including instruments | 75 | 75 | 9344.46 | 129811.2789
5075-Blade Path Temperature Spread A | 204 | 203 | 36282.7 | 392752.704
5079-Other combustor problems B | 320 | 298 | 42861.11 | 629741.155
5080-High pressure shaft C | 11 | 11 | 1927.1 | 852470.5093
5081-High pressure bearings D | 42 | 42 | 2489.72 | 780171.9437
5082-High pressure blades/buckets A | 5 | 5 | 1105.29 | 420673.0474
5083-High pressure nozzles/vanes A | 7 | 7 | 383 | 4338.4832
5084-High pressure casing/expansion joints | 2 | 2 | 376 | 4026.3332
5085-Interstage gas passages - HP | 1 | 1 | 330 | 170.4998
5086-High pressure shaft seals A | 3 | 3 | 454.4 | 50741.3465
5087-Thrust Bearing | 5 | 5 | 234.4 | 10349.1133
5088-Gas turbine cooling steam | 37 | 37 | 9050.29 | 289793.835
5089-Other high pressure problems B | 17 | 17 | 1666.46 | 4141.9218
5090-Low pressure shaft A | 4 | 4 | 42 | 165.2
5091-Low pressure bearings A | 2 | 2 | 98 | 2990.1666
5092-Low pressure blades/buckets D | 4 | 4 | 170 | 580494.4166
5093-Low pressure nozzles/vanes B | 2 | 2 | 137.7 | 414.24
5094-Low pressure casing/expansion joints A | 1 | 1 | 105.5 | 5980.0916
5096-Low pressure shaft seals | 1 | 1 | 40 | 8360
5097-Other low pressure problems B | 9 | 9 | 1002.08 | 489063.0159
5098-Expansion joints A | 2 | 2 | 390 | 8638.8
5100-Chamber A | 8 | 8 | 1452.31 | 61273.0254
5102-Vanes/nozzles A | 7 | 7 | 1247.7 | 149028.898
5103-Silencer B | 1 | 1 | 122 | 368.0333
5104-Cones A | 2 | 2 | 260 | 22355.6666
5105-Diverter Dampers B | 9 | 9 | 823 | 7370.8165
5106-Exhaust Stack | 13 | 13 | 1447.15 | 107290.3538
5108-High engine exhaust temperature A | 141 | 125 | 12305.49 | 129878.2088
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 228 | 227 | 29644.61 | 632994.9765
5110-Lube oil system - general | 202 | 202 | 15115.72 | 992956.1888
5111-Lube oil pumps B | 84 | 84 | 10874.64 | 235608.2729
5112-Lube oil coolers B | 29 | 29 | 2159.36 | 13274.8144
5113-Lube oil valves/piping | 33 | 33 | 2982.91 | 97648.7384
5114-Lube oil filters | 13 | 13 | 970.45 | 18866.014
5115-Oil vapor extractor | 18 | 18 | 1602.46 | 5915.3944
5116-Power Augmentation System Equipment B | 2 | 2 | 72 | 22320
5118-Power augmentation valves | 7 | 7 | 682.56 | 3297.4674
5119-Power augmentation controls | 4 | 4 | 82 | 367.5667
5120-Hydraulic oil system A | 107 | 107 | 11386.16 | 227871.6984
5121-Hydraulic oil system pumps | 22 | 22 | 2287.55 | 46215.9769
5122-Hydraulic oil system piping/valves | 29 | 29 | 3328.46 | 101259.458
5130-Starting system (including motor) A | 320 | 320 | 40335.05 | 1915782.2351
5140-Battery and charger system B | 16 | 16 | 1047.69 | 8126.9503
5150-Turning gear and motor C | 63 | 63 | 6705.9 | 527672.4647
5151-Load gear compartment B | 2 | 2 | 135 | 29520.4166
5160-Cooling and seal air system B | 172 | 171 | 22283.47 | 307964.1857
5170-Cooling water system A | 40 | 40 | 4655.44 | 118649.1004
5180-Anti-icing system A | 7 | 7 | 396.72 | 3728.0007
5190-Other auxiliary system problems A | 160 | 156 | 14820.12 | 487469.8962
5200-Reduction gear B | 8 | 8 | 381.75 | 76549.2999
5201-Load shaft and bearings A | 11 | 11 | 1401.5 | 120847.0079
5205-Main coupling between the turbine and generator A | 1 | 1 | 143 | 6825.8666
5206-Gas Turbine Clutch | 23 | 23 | 1795.5 | 193001.7094
5210-Intercoolers A | 13 | 12 | 1119.6 | 11823.513
5230-Heat shields C | 2 | 2 | 279 | 1534.5
5240-Fire detection and extinguishing system B | 211 | 210 | 25858.45 | 444045.5771
5241-Fire in unit A | 12 | 12 | 1329 | 727513.413
5245-Gas Turbine Control System - data highway | 35 | 35 | 4166.2 | 47973.1427
5246-Gas Turbine Control System - hardware problems (including card failure) | 208 | 208 | 25339.5 | 303579.9036
5247-Gas Turbine Control System - internal and termination wiring | 30 | 30 | 3420.11 | 23649.1769
5248-Gas Turbine Control System - logic problems | 92 | 91 | 11919.26 | 83397.5937
5249-Gas Turbine Control System - upgrades | 12 | 12 | 1238 | 4100.0159
5250-Other Controls and instrumentation Problems A | 525 | 519 | 60283.2 | 777680.2832
5255-Computer | 8 | 8 | 723.8 | 4173.7048
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 3 | 3 | 202.3 | 65336.5065
5261-Gas turbine/compressor washing | 26 | 26 | 2763.55 | 18606.4465
5262-Gas turbine exchange | 3 | 3 | 45.9 | 1703.825
5269-Combustion inspection (CI) | 6 | 6 | 1219.2 | 213289.9661
5270-Hot end inspection B | 5 | 5 | 629.3 | 46652.4631
5272-Boroscope inspection A | 16 | 16 | 1547.4 | 46874.7347
5274-General unit inspection A | 30 | 29 | 3747.83 | 179808.6197
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 59 | 59 | 5984.54 | 97918.3517
5285-Gas turbine vibration | 243 | 242 | 21547.18 | 2817674.2798
5286-Gas Turbine lockout cause by OEM specifications | 11 | 11 | 677.85 | 7782.1182
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 16 | 12 | 234.21 | 254.183
5295-Synchronous condenser equipment A | 2 | 2 | 171 | 464.5499
5298-Main gas filter | 5 | 5 | 470.5 | 5731.7083
5299-Other miscellaneous gas turbine problems | 442 | 429 | 39333.46 | 2491360.3539
5400-Inlet air ducts B | 1 | 1 | 88 | 264
5401-Inlet air vanes/noozles | 7 | 7 | 322.16 | 2231.1786
5402-Inlet air filters B | 14 | 14 | 455.46 | 16979.7859
5404-Inlet air chillers A | 7 | 7 | 117 | 5206.8333
5405-Inlet air evaporative coolers A | 2 | 2 | 57.4 | 363.5333
5406-Inlet air foggers A | 6 | 6 | 33.5 | 633.0333
5409-Other inlet air problems B | 22 | 22 | 916.52 | 5554.945
5410-High pressure shaft B | 1 | 1 | 49.5 | 18710.175
5411-High pressure bearings B | 1 | 1 | 32.1 | 104.325
5412-High pressure blades/buckets C | 5 | 5 | 405.1 | 82180.9965
5413-Other high pressure problems D | 10 | 10 | 324.64 | 2435.9926
5414-Compressor diaphragms/vanes | 4 | 4 | 168.3 | 29147.5899
5420-Low pressure shaft C | 3 | 3 | 315.6 | 11367.9666
5422-Low pressure blades/buckets C | 1 | 1 | 46 | 38169.2666
5429-Other low pressure problems D | 20 | 17 | 973.9 | 16534.0114
5439-Jet engine other compressor problems | 57 | 52 | 3056.95 | 24949.7757
5441-Fuel piping and valves B | 144 | 144 | 7160.58 | 38995.8981
5442-Fuel nozzles/vanes A | 5 | 5 | 436.4 | 18303.1165
5444-Liquid fuel oil pump B | 2 | 2 | 98.4 | 5132.38
5445-Liquid fuel oil transfer/forwarding pump A | 2 | 2 | 119.4 | 253.3133
5446-Liquid fuel purge system B | 7 | 7 | 381.2 | 1497.6398
5447-Gas fuel system A | 174 | 172 | 14473.49 | 44198.1557
5449-Other fuel system problems A | 74 | 72 | 2990.6 | 11322.7907
5450-Ignition system B | 25 | 25 | 1606.32 | 13557.0957
5451-Pilot fuel piping and valves B | 1 | 1 | 44 | 10.2667
5454-Water injection system (Jet Engine) | 66 | 66 | 3081.45 | 36626.1724
5455-Fuel nozzle/vane cooling air system | 7 | 7 | 168 | 2004
5470-Combustor casing B | 2 | 2 | 54.3 | 85057.9166
5473-Flame scanners A | 9 | 8 | 662 | 3070.9831
5475-Blade Path Temperature Spread B | 36 | 35 | 4663.34 | 29562.5288
5479-Other combustor problems A | 28 | 28 | 1958.75 | 34427.6408
5480-High pressure shaft A | 1 | 1 | 19.86 | 2.979
5481-High pressure bearings A | 1 | 1 | 49.6 | 4315.2
5482-High pressure blades/buckets D | 6 | 6 | 238.5 | 102146.3916
5484-High pressure casing/expansion joint | 1 | 1 | 40 | 160
5485-Interstage gas passages | 1 | 1 | 13 | 14.5167
5487-Thrust Bearing/jet | 6 | 6 | 396.5 | 1868.7832
5489-Other high pressure problems C | 3 | 3 | 167 | 10278.6333
5491-Low pressure bearings C | 1 | 1 | 46 | 282.9
5492-Low pressure blades/buckets B | 2 | 2 | 90 | 2844
5494-Low pressure casing/expansion joints B | 1 | 1 | 23 | 45170.85
5497-Other low pressure problems C | 7 | 7 | 322.5 | 865.3299
5499-Shaft seals A | 1 | 1 | 43 | 45883.8666
5505-Diverter Dampers A | 34 | 34 | 247 | 1210.1
5508-High engine exhaust temperature B | 23 | 22 | 578.21 | 6397.8627
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 27 | 27 | 1653.83 | 11476.1817
5510-Lube oil system A | 147 | 147 | 6980.85 | 219726.3601
5516-Power Augmentation System Equipment A | 11 | 11 | 601.1 | 95354.4516
5520-Hydraulic oil system B | 31 | 31 | 1516.5 | 10145.9162
5530-Starting system (including motor) B | 43 | 43 | 1938.81 | 29879.7267
5540-Battery and charger system A | 7 | 7 | 221.94 | 8236.5041
5550-Turning gear and motor B | 2 | 2 | 278 | 22327.9333
5560-Cooling and seal air system A | 28 | 28 | 1247.85 | 37551.9206
5570-Cooling water system B | 7 | 7 | 567 | 12448.5999
5580-Anti-icing system B | 31 | 31 | 541.9 | 2488.3215
5590-Other auxiliary system problems B | 76 | 73 | 2973.9 | 21085.7591
5600-Reduction gear A | 1 | 1 | 51 | 139.4
5605-Main coupling between the turbine and generator B | 2 | 2 | 140 | 452.4
5606-Jet Engine Clutch | 15 | 15 | 1305.6 | 5337.9779
5610-Intercoolers B | 2 | 2 | 214 | 821.7
5630-Heat shields A | 1 | 1 | 52 | 730.6
5640-Fire detection and extinguishing system A | 45 | 44 | 2588 | 41007.4018
5641-Fire in unit B | 2 | 2 | 131.6 | 3577.0883
5645-Jet Engine Control System - data highway | 19 | 18 | 906.25 | 7750.7582
5646-Jet Engine Control System - hardware problems (including card failure) | 66 | 66 | 3244.6 | 26700.9274
5647-Jet Engine Control System - internal and termination wiring | 23 | 22 | 904 | 2765.8497
5648-Jet Engine Control System - logic problems | 31 | 31 | 1382.56 | 9429.5565
5650-Other Controls and instrumentation Problems B | 181 | 179 | 7357.95 | 53976.6294
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 1 | 1 | 52 | 15159.7333
5661-Engine/compressor washing | 3 | 3 | 105 | 392.5833
5662-Engine exchange | 1 | 1 | 22 | 14894
5665-Engine shafts and bearings | 3 | 3 | 241.7 | 1795.1466
5670-Hot end inspection A | 2 | 1 | 207 | 3.4499
5672-Boroscope inspection B | 5 | 5 | 283.7 | 5847.0048
5674-General unit inspection B | 29 | 28 | 1465.96 | 477691.3974
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 18 | 18 | 885.09 | 12930.0087
5685-Engine vibration | 80 | 80 | 3489.55 | 124619.8331
5686-Jet Engine lockout cause by OEM specifications | 6 | 6 | 193.21 | 1749.7626
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 20 | 16 | 325 | 2225.0999
5692-Turbine Overspeed Trip Test - Jet Engine | 2 | 2 | 84 | 1440.6
5695-Synchronous condenser equipment B | 1 | 1 | 17 | 215.6167
5699-Other miscellaneous jet engine problems | 59 | 58 | 3030.69 | 856906.3933
5700-Drive shaft and bearings | 1 | 1 | 7 | 3073
5710-Cylinders | 11 | 11 | 256.44 | 36890.81
5711-Cylinder heads | 7 | 7 | 149.34 | 8239.0796
5730-Intake valves | 2 | 2 | 18.08 | 128.5187
5731-Exhaust valves | 6 | 6 | 61 | 772.9833
5734-exhaust gas bellow | 2 | 2 | 46.78 | 5928.0013
5740-Turbo charger | 1 | 1 | 9.04 | 45.2
5759-waste gate | 2 | 2 | 46.78 | 6291.0896
5762-crankshaft | 1 | 1 | 9 | 64.5
5790-Vibration | 3 | 3 | 159 | 578.5833
5799-Other engine problems | 20 | 20 | 256.78 | 8723.9415
5800-Lube oil system C | 9 | 9 | 116.32 | 7469.3574
5801-Lube oil separator | 2 | 2 | 11 | 4433
5805-Cooling system | 31 | 31 | 352.93 | 17417.4449
5815-Fuel system | 29 | 26 | 432.8 | 1855.3441
5820-Start system | 7 | 7 | 120.66 | 2720.9933
5831-Exhaust gas rapture disc | 4 | 4 | 122.26 | 3141.852
5832-Turning gear | 2 | 2 | 38.04 | 195.788
5849-Other engine auxiliaries problems | 5 | 5 | 41.61 | 1806.5238
5855-Engine control system | 29 | 29 | 455.71 | 12571.313
5865-Synchronization system | 1 | 1 | 9.04 | 167.24
5870-Other engine control problems | 3 | 3 | 24.18 | 1137.8175
5873-Gas admission valve | 5 | 5 | 161.46 | 419.157
5895-Inspection C | 1 | 1 | 19.04 | 1599.36
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 259 | 251 | 6826.69 | 64844.0842
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 29 | 29 | 4798.5 | 66142.24
6005-HP Evaporator tubes | 11 | 11 | 1378.75 | 101785.308
6006-IP Evaporator tubes | 2 | 2 | 372 | 18872.7999
6007-LP Evaporator tubes | 4 | 4 | 931 | 82150.8666
6010-HP superheater | 41 | 41 | 5022.7 | 473938.135
6011-HP reheater | 16 | 16 | 2041.75 | 164952.9453
6012-HP economizer | 22 | 22 | 2538.81 | 109674.447
6020-IP superheater | 8 | 8 | 1223.94 | 93699.6824
6021-IP reheater | 15 | 15 | 2154 | 146802.8661
6022-IP economizer | 2 | 2 | 145 | 7015.85
6032-LP economizer | 9 | 9 | 1156.19 | 148071.4087
6090-Other HRSG tube Problems | 12 | 12 | 2412.28 | 172681.1179
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 4 | 4 | 732 | 1279.4
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 25 | 25 | 5153.02 | 599669.7955
6111-HP steam relief/safety valves | 11 | 11 | 717.4 | 5049.3066
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 30 | 30 | 7908.24 | 103117.6597
6113-Other HP steam system problems | 13 | 13 | 1843.5 | 7285.5331
6114-HP steam isolation/boundary valves | 37 | 37 | 8843.53 | 469878.0489
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 1 | 1 | 310.5 | 569.2499
6121-IP steam relief/safety valves | 7 | 7 | 1694.85 | 45484.9
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 6 | 6 | 853.36 | 19537.1693
6123-Other IP steam system problems | 3 | 3 | 310 | 3137.7998
6124-IP steam isolation/boundary valves | 13 | 13 | 2428.69 | 13948.1745
6131-LP steam relief/safety valves | 3 | 3 | 950 | 4161.7828
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 6 | 6 | 742 | 4560.6331
6133-Other LP steam system problems | 18 | 18 | 1323.89 | 9487.5855
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 31 | 31 | 5228.56 | 52452.0164
6135-LP steam isolation/boundary valves | 2 | 2 | 650 | 102.9164
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 7 | 7 | 1218.5 | 47990.4828
6141-HP Desuperheater/attemperator valves | 47 | 47 | 7728.91 | 117064.325
6142-HP Desuperheater/attemperator spray nozzles | 9 | 9 | 2018 | 75173.3327
6144-Other HP desuperheater/attemperator problems | 32 | 32 | 4948.47 | 88373.1855
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 1 | 1 | 297.6 | 30499.0399
6146-IP Desuperheater/attemperator valves | 15 | 15 | 3255.2 | 11844.3204
6147-IP Desuperheater/attemperator spray nozzles | 4 | 4 | 1495.3 | 57170.8944
6149-Other IP desuperheater/attemperator problems | 2 | 2 | 324 | 12478.1499
6153-LP Desuperheater/attemperator drums | 1 | 1 | 143.8 | 1107.26
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 7 | 7 | 1561.25 | 28169.4788
6161-HP Startup bypass system valves | 58 | 58 | 13852.66 | 552724.4097
6163-Other HP startup bypass system problems | 6 | 6 | 2535.53 | 25323.4627
6164-HP Startup bypass instrumentation and controls | 11 | 11 | 3037 | 39551.5158
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 3 | 3 | 606 | 30388.1666
6171-IP Startup bypass system valves | 24 | 24 | 5147.72 | 27115.0905
6173-Other IP startup bypass system problems | 4 | 4 | 1689.5 | 3924.8822
6174-IP Startup bypass instrumentation and controls | 8 | 8 | 1760.8 | 18719.1459
6181-LP Startup bypass system valves | 2 | 2 | 437 | 384.483
6184-LP startup bypass instrumentation and controls | 1 | 1 | 265 | 1810.8332
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 111 | 111 | 20355.56 | 165559.2109
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 25 | 25 | 3111.06 | 26078.8838
6399-Other coal gasification equipment problems | 130 | 130 | 14071.32 | 487213.8424
6410-Steam wells/steam field piping problems | 5 | 5 | 92 | 2462.3666
6420-Condensate reinjection system | 15 | 15 | 110 | 32453.5833
6430-Unit H2S emission limitations ? regulatory | 1 | 1 | 49 | 369.1333
6440-H2S abatement system problems ? general | 12 | 12 | 249 | 1296.7499
6499-Geothermal | 6 | 6 | 107 | 256.0166
7000-Shaft B | 5 | 5 | 194.65 | 229669.1883
7001-Shaft packing | 34 | 34 | 2249.25 | 284009.0753
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 30 | 30 | 1631.21 | 100190.3023
7007-Bearings A | 30 | 30 | 2238.53 | 601023.782
7008-Bearing cooling system B | 34 | 34 | 1844.92 | 70454.8557
7009-Bearing Oil System | 62 | 62 | 4249.1 | 50021.879
7010-Runner cavitation damage | 8 | 8 | 222.26 | 46556.331
7011-Other runner problems | 8 | 8 | 571.7 | 382339.5947
7014-Blade or bucket cracking | 1 | 1 | 19.6 | 42786.8
7020-Nozzle assembly | 2 | 2 | 73.8 | 808.38
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 38 | 36 | 2096.16 | 288747.5612
7040-Turbine overhaul | 1 | 1 | 113.41 | 151.2133
7050-Turbine governor | 154 | 154 | 11660.58 | 282943.6877
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 92 | 78 | 3992.28 | 645469.6921
7053-Governor Oil System | 80 | 80 | 5135.47 | 61946.1107
7070-Speed Increaser | 8 | 8 | 267.8 | 233.5249
7099-Other turbine problems | 69 | 68 | 5693.59 | 550484.2617
7100-Upper reservoir dams and dikes | 3 | 3 | 110 | 45.4833
7101-Lower reservoir dams and dikes | 19 | 19 | 666.6 | 9251.4898
7110-Intake channel or flume (including trash racks) | 87 | 86 | 2886.85 | 296104.4918
7111-Intake tunnel | 14 | 14 | 1316.5 | 56536.0078
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 4 | 4 | 8.5 | 31.5917
7120-Headgates | 35 | 35 | 2049.89 | 119681.496
7121-Shutoff valves | 28 | 28 | 5185.94 | 67003.2011
7123-Shutoff valve bypass line and valve | 7 | 7 | 514.3 | 15184.7883
7124-Penstock | 12 | 12 | 692.88 | 13222.8289
7130-Spiral case | 2 | 2 | 87.8 | 1435.9833
7140-Wicket gate assembly | 8 | 8 | 243.07 | 139711.1324
7141-Wicket gate operating mechanism or positioner | 25 | 25 | 2391.86 | 87775.4213
7142-Wicket gate shear pin | 126 | 126 | 7237.15 | 88286.7833
7160-Pressure regulating valve | 3 | 3 | 125.74 | 299.2363
7161-Pressure regulating valve operator or positioner | 2 | 2 | 146.72 | 1722.112
7162-Relief valve and vacuum breakers | 5 | 5 | 570.66 | 4939.604
7170-Draft tube | 559 | 528 | 6892 | 78768.9811
7180-Tailrace | 24 | 24 | 899 | 71524.0539
7181-Tail water depressing equipment | 11 | 11 | 588.8 | 1804.5765
7190-Dewatering and rewatering equipment | 10 | 10 | 1162.55 | 47684.5754
7191-Equalizing line | 1 | 1 | 42.56 | 1300.208
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 128 | 128 | 3445.16 | 302789.2903
7201-Inspection A | 7 | 7 | 384.75 | 7091.0457
7210-Canals (including siphons; radial gates; and spills) | 6 | 6 | 80.1 | 2534.6467
7220-Unit out of service due to common penstock with unit under repair | 5 | 5 | 329.4 | 3687.2849
7230-Pony motor (pumped storage units only) | 2 | 2 | 633 | 23752.1166
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 35 | 35 | 3561.98 | 77629.8079
7800-Couplings | 2 | 2 | 64 | 15138.6667
7820-Bearings B | 1 | 1 | 26 | 22.9667
7830-Blades | 5 | 5 | 58 | 65568
7860-Nozzles/vanes | 1 | 1 | 51 | 251.6
7900-Inner casing D | 1 | 1 | 251.5 | 16167.2583
7910-Outer exhaust casing | 1 | 1 | 209 | 3932.6832
7920-Lube oil system B | 11 | 11 | 363.2 | 5825.0298
7930-Controls and instrumentation A | 24 | 24 | 2017.39 | 39185.4686
7950-Major overhaul B | 4 | 4 | 463.5 | 208484.8831
8000-Chemical feed storage; mill feeders; and conveyors | 11 | 11 | 5039 | 13701.3152
8002-Screw conveyors | 2 | 2 | 1475 | 9723.3324
8010-Crushers/mills | 21 | 21 | 10782.37 | 38226.6525
8020-Mill slurry tanks supply problems | 9 | 9 | 1595 | 2340.666
8030-Classifiers | 1 | 1 | 60 | 123
8040-Slurry transfer pumps and motors | 5 | 5 | 354.08 | 1047.9066
8099-Other chemical supply problems | 11 | 11 | 1714.41 | 38095.3242
8100-Scrubber/absorber tower or module | 43 | 43 | 7113.98 | 120887.7197
8110-Spray nozzles | 2 | 2 | 260 | 670
8115-Disc scrubber throats | 1 | 1 | 47 | 1543.1667
8120-Spray pumps and motors | 26 | 26 | 6054 | 53420.5648
8125-Scrubber recycle (liquid) pumps | 16 | 16 | 2653.26 | 108253.2188
8127-Scrubber recycle (liquid) pump motors | 5 | 5 | 860.3 | 2258.4278
8130-Recirculation tanks including agitators | 6 | 5 | 2880 | 294931.4992
8140-Reaction tanks including agitators | 4 | 4 | 1357.1 | 181255.0345
8150-Tubes | 1 | 1 | 243 | 20096.1
8160-Mist eliminators/demisters and washdown | 50 | 43 | 6098.51 | 805476.8453
8199-Other scrubber problems | 29 | 29 | 5945.43 | 95922.1376
8200-Piping | 14 | 14 | 2439.5 | 16676.9663
8210-Valves | 6 | 6 | 1363 | 11848.8662
8230-Ducting | 5 | 5 | 1723.9 | 244818.7161
8235-Demister | 17 | 15 | 351 | 342.4499
8240-Bypass dampers | 2 | 2 | 589 | 2358.7331
8250-Dampers other than bypass | 3 | 3 | 543.77 | 25914.1065
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 14 | 14 | 1685.27 | 12861.2315
8261-Scrubber booster I.D. fan drive | 13 | 13 | 2384.5 | 37771.371
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 13 | 13 | 3262 | 131818.916
8265-Scrubber ID fan dampers | 1 | 1 | 225 | 1139.9998
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 5 | 5 | 695.25 | 146821.4456
8271-Scrubber booster F.D. fan drive | 2 | 2 | 380 | 1162.1665
8280-Reagent feed piping | 3 | 3 | 344 | 4184.3665
8299-Other piping; ducting; damper; and fan problems | 4 | 4 | 1788 | 34383.3829
8300-Waste disposal/recovery tanks | 1 | 1 | 150 | 699.9999
8330-Dewatering equipment (thickener; centrifuge; etc.) | 9 | 9 | 2989.46 | 228309.1493
8340-Centrifuge/vacuum filter | 2 | 2 | 751.98 | 17772.4366
8349-Other waste disposal and recovery problems | 6 | 6 | 1705 | 109370.4764
8399-Solids conveying and mixing system problems | 5 | 5 | 2999.35 | 31542.4434
8410-Scrubber instruments and controls | 10 | 10 | 893.83 | 6355.7841
8415-Liquid level controls | 6 | 6 | 931.6 | 10917.0947
8426-Miscellaneous electrical failures | 5 | 5 | 204.4 | 3794.4933
8430-Stack damage related to scrubber system | 1 | 1 | 627 | 74372.6496
8440-Major overhaul | 1 | 1 | 198 | 1352.9999
8450-Inspection | 1 | 1 | 70 | 215.8333
8470-SO2 monitor | 3 | 3 | 207 | 1313.2166
8499-Other miscellaneous wet scrubber problems | 96 | 96 | 3400.19 | 29194.2605
8500-Slurry storage and feed tanks | 6 | 6 | 453 | 2704.8332
8501-Reagent storage; feed bins; and conveyors | 6 | 6 | 1635 | 74431.3997
8506-Slurry pipelines | 5 | 5 | 226.6 | 1430.9749
8507-Reagent uploading and transfer systems | 2 | 2 | 208 | 1158.6666
8510-Slurry mixers and agitators | 8 | 8 | 496.8 | 12404.8665
8521-Reagent/slurry problems | 5 | 5 | 1095.5 | 34041.3245
8522-Piping | 1 | 1 | 100 | 280
8523-Valves | 3 | 3 | 438 | 4414.3999
8525-Ducting | 3 | 3 | 178 | 32634.75
8527-Other piping; ducting; and damper problems | 5 | 5 | 765 | 190935.6664
8530-Spray towers | 2 | 2 | 594 | 501280.3996
8531-Spray machine/atomizer | 65 | 65 | 8973.6 | 91265.2474
8532-Spray machine/atomizer motors | 3 | 3 | 94.6 | 13044.8666
8534-Spray machine/atomizer vibration problems | 26 | 26 | 3887 | 60054.7483
8535-Fly ash conveyors | 9 | 9 | 463.98 | 4253.7668
8538-Recycle storage and feed tanks including agitators | 1 | 1 | 197 | 1182
8544-Mechanical failures | 7 | 7 | 454 | 9695.6499
8545-Electrical failures | 9 | 9 | 1638.15 | 13380.9013
8547-Inspection | 5 | 5 | 490.7 | 1055.4582
8548-Testing | 2 | 2 | 482 | 938.1998
8549-Other dry scrubber problems | 19 | 19 | 4868.6 | 90464.8789
8550-Electrostatic precipitator fouling | 32 | 32 | 3721.93 | 261524.2601
8551-Electrostatic precipitator field out of service | 54 | 54 | 6093.08 | 123937.1743
8560-Electrostatic precipitator problems | 55 | 55 | 8916.69 | 435413.1462
8565-Electrostatic Precipitator rebuild/overhaul | 1 | 1 | 163.79 | 3791.7385
8570-Mechanical precipitator fouling | 16 | 16 | 1732 | 126974.8496
8590-Other precipitator problems | 14 | 13 | 1908.5 | 11738.1745
8600-Flue gas additives (furnace injection) | 1 | 1 | 375 | 2356.2499
8601-SO3 mitigation | 12 | 12 | 2225 | 8918.0829
8620-Mercury Abatement | 13 | 13 | 1818.32 | 28790.7725
8650-Baghouse systems; general | 375 | 374 | 21118.69 | 1007569.138
8651-Bag failures and rebagging | 124 | 124 | 8731.34 | 248214.457
8654-Baghouse booster fans and motors | 45 | 45 | 3806.12 | 95976.5179
8655-Structural duct work and dampers | 5 | 5 | 281 | 46726.4999
8656-Controls and instrumentation B | 50 | 50 | 4182.18 | 86047.7021
8657-Ash handling system and hoppers | 27 | 27 | 4397.95 | 341091.2928
8670-Emission monitors (other than CEMS) A | 2 | 2 | 197.3 | 591.9
8699-Other miscellaneous pollution control equipment problems | 25 | 25 | 4609.6 | 184592.3885
8700-CEMS Certification and Recertification | 60 | 59 | 6228.73 | 32429.8766
8710-SO2 analyzer problems | 1 | 1 | 100 | 118.3333
8720-NOx analyzer problems | 57 | 57 | 4955.5 | 49353.3546
8730-CO analyzer problems | 38 | 38 | 2994.37 | 49637.6933
8740-CO2 analyzer problems | 7 | 7 | 796.05 | 73533.623
8750-O2 analyzer problems | 15 | 15 | 1193.61 | 7837.8724
8760-Opacity monitor problems | 4 | 4 | 436 | 3753.1333
8770-Flow monitor problems | 14 | 14 | 1740.52 | 17241.483
8780-Data acquisition system problems | 34 | 33 | 2963.5 | 47000.0658
8790-Miscellaneous CEMS problems | 163 | 162 | 11793.21 | 166374.6485
8800-SNCR NOx Reagent | 1 | 1 | 167.23 | 1886.9118
8802-SNCR NOx Control system | 15 | 15 | 1027.87 | 4930.493
8803-Sncr Performance Testing | 6 | 6 | 319.5 | 4293.5
8809-Other SNCR NOx problems | 45 | 45 | 1973.65 | 54797.4542
8810-SCR NOx Reactor | 6 | 6 | 656 | 9856.3996
8812-SCR NOxCatalyst | 3 | 3 | 102 | 114.0833
8813-SCR NOx Injection grid piping/valves | 38 | 38 | 5085.82 | 31818.7368
8814-SCR NOx Catalyst support material | 2 | 2 | 103.79 | 666.7588
8815-SCR NOx Soot blowers | 2 | 2 | 198.4 | 709.2799
8816-SCR NOx Plugging | 16 | 16 | 1002.66 | 630206.6746
8817-SCR NOx Control system | 68 | 68 | 8028.65 | 43023.3649
8820-SCR NOx Ammonia injection grid piping/valves | 68 | 67 | 5767.93 | 78381.5358
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 34 | 34 | 2117.06 | 11111.7962
8822-SCR NOx Ammonia air blowers | 36 | 36 | 2563 | 15295.6057
8823-SCR NOx Other ammonia system problems | 74 | 74 | 8717.23 | 156382.0555
8825-Other SCR NOx problems | 57 | 57 | 4167.39 | 57857.6723
8830-CAH NOx Active catalyst | 2 | 2 | 203.8 | 10614.5833
8831-CAH NOx Support materials | 1 | 1 | 7.5 | 232
8835-CAH NOx Other CAH problems | 2 | 2 | 261 | 487.1998
8840-CO Active catalyst | 9 | 9 | 253 | 8398.3499
8845-Other CO reduction problems | 68 | 68 | 5518.49 | 50385.5372
9000-Flood | 86 | 86 | 3087.04 | 2308750.4599
9010-Fire; not related to a specific component | 82 | 82 | 5079.05 | 1617637.6978
9015-Pandemic | 90 | 88 | 12905.72 | 6412908.9934
9020-Lightning | 125 | 125 | 17399.79 | 395700.9563
9030-Earthquake | 8 | 8 | 186 | 505.9166
9031-Tornado | 1 | 1 | 219 | 2671.8
9035-Hurricane | 97 | 97 | 17737.98 | 4449440.4539
9036-Storms (ice; snow; etc) | 139 | 139 | 11297.97 | 1968933.7432
9040-Other catastrophe | 15 | 15 | 2592.58 | 245932.7937
9110-Core coastdown (nuclear) | 4 | 4 | 509.85 | 197572.0667
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 439 | 433 | 37368.5 | 2479319.4137
9131-Lack of fuel: Contract or Tariff allows for interruption | 352 | 310 | 42070.59 | 1045997.7377
9132-Wet Fuel - Biomass | 264 | 250 | 1607.51 | 17153.8564
9134-Fuel conservation | 52 | 52 | 7492 | 239097.7495
9135-Lack of water (hydro) | 2552 | 2317 | 33303.64 | 1284344.7838
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 37 | 37 | 7336.98 | 10773.7391
9137-Ground water or other water supply problems | 56 | 56 | 4715.91 | 239152.7823
9180-Economic (for internal use at plants only) | 1 | 1 | 36.77 | 440.6272
9181-Economic (for internal use at plants only) | 2 | 2 | 999 | 2362.7164
9182-Economic (for internal use at plants only) | 18 | 18 | 7721 | 20864.3647
9200-High ash content | 70 | 70 | 2845 | 84392.4324
9205-Poor quality natural gas fuel; low heat content | 11 | 11 | 1811.5 | 3189.3575
9210-Low grindability | 4 | 4 | 329.28 | 1276.1626
9220-High sulfur content | 15 | 15 | 535 | 1728.0831
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 141 | 141 | 2934.99 | 56289.6842
9251-Low Btu Coal From Contract For Low Btu Coal | 67 | 63 | 1922.89 | 43261.5337
9260-Low Btu oil | 1 | 1 | 10 | 62.1667
9261-Low Btu oil (not outside management control) | 2 | 2 | 74.5 | 705.9666
9270-Wet coal | 438 | 423 | 59547.88 | 1504961.5841
9271-Wet coal (not outside management control) | 278 | 277 | 47929.81 | 492216.4297
9272-Wet Fuel (other than coal) | 9 | 9 | 93 | 97
9280-Frozen coal | 1 | 1 | 47 | 47
9281-Frozen coal (not outside management control) | 3 | 3 | 1155 | 2817.8332
9290-Other fuel quality problems | 110 | 105 | 10350.28 | 263350.6127
9291-Other fuel quality problems (not outside management control) | 97 | 97 | 2185.06 | 15493.328
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 1040 | 1035 | 76172.84 | 2926466.9885
9305-Ash disposal problem | 3 | 3 | 594.18 | 52919.0203
9310-Operator training | 2 | 2 | 656.49 | 5669.6331
9320-Other miscellaneous external problems | 983 | 843 | 38637.93 | 2306978.9513
9340-Synchronous Condenser Operation | 2 | 2 | 166.05 | 113.7016
9345-Pumping Operations | 2 | 2 | 50 | 698.3333
9350-Public Safety/River Rescue | 11 | 11 | 485.9 | 609.8044
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 4 | 4 | 1058 | 2311642.5
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 44 | 44 | 1867.88 | 37971.0238
9600-SO2 stack emissions (fossil) | 254 | 171 | 7957.4 | 75310.4811
9610-NOx stack emissions (fossil) | 10 | 10 | 1029.91 | 24720.7497
9613-NOx stack emissions (gas turbine) | 136 | 135 | 9606.43 | 169166.4039
9614-NOx stack emissions (jet engines) | 29 | 29 | 1377.75 | 12353.037
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 1 | 1 | 2.57 | 207.9987
9616-CO stack emissions | 174 | 142 | 6928 | 69009.9084
9620-Particulate stack emissions (fossil) | 17 | 17 | 1599.7 | 130458.8311
9630-Opacity (fossil) | 515 | 503 | 40907.98 | 839855.2762
9633-Opacity (gas turbine) | 1 | 1 | 215 | 5765.5832
9650-Other stack or exhaust emissions (fossil) | 72 | 72 | 1195 | 46081.6329
9653-Other stack or exhaust emissions (gas turbine) | 34 | 34 | 3935.69 | 50477.4617
9654-Other stack or exhaust emissions (jet engines) | 9 | 9 | 435.5 | 21953.7082
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 4 | 4 | 45.75 | 689.9667
9656-Other stack or exhaust emissions testing - fossil | 13 | 13 | 1596.63 | 13464.9964
9657-Other stack or exhaust emissions testing - gas turbine | 8 | 8 | 503.61 | 25808.9764
9660-Thermal discharge limits (fossil and nuclear) | 65 | 64 | 6710.5 | 122100.8862
9663-Thermal discharge limits (gas turbine) | 1 | 1 | 147 | 88.2
9686-Fish kill (hydro and PS) | 1 | 1 | 155 | 330.6666
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 124 | 124 | 9722.6 | 1427063.3561
9693-Other miscellaneous operational environmental limits (gas turbines) | 45 | 42 | 4136.8 | 24907.0476
9694-Other miscellaneous operational environmental limits (jet engines) | 45 | 43 | 825.77 | 4641.039
9696-Other miscellaneous operational environmental limits (hydro and PS) | 16 | 16 | 313.87 | 207161.2364
9700-OSHA-related retrofit or inspection | 2 | 2 | 241 | 77132.05
9720-Other safety problems | 52 | 52 | 4073.35 | 1533781.2916
9900-Operator error | 407 | 407 | 83650.13 | 618889.5791
9910-Maintenance personnel error | 103 | 103 | 20981.5 | 146916.6005
9920-Contractor error | 57 | 55 | 12644.24 | 323344.1619
9930-Operating procedure error | 35 | 35 | 10385.55 | 127207.0194
9940-Maintenance procdure error | 9 | 9 | 1696.22 | 10062.6986
9950-Contractor procedure error | 22 | 22 | 3675.45 | 61817.0516
9960-Staff shortage | 24 | 24 | 4181.85 | 681637.4768
9997-NERC Reliability Standards requirements | 2 | 2 | 46 | 242.8333
9998-Black Start testing | 4 | 4 | 297 | 3033.8
9999-Total unit performance testing (use appropriate codes for individual component testing) | 232 | 225 | 8379.96 | 4710136.9972
Total Result | 52754 | 51441 | 6395584.65 | 341252806.7295

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0000 | Reserve shutdown | External | Economic | U2 | Forced - Delayed | 2020 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Summer | 771.8399 | 172.8 | 1 | 2 | 0000-Reserve shutdown | U2-Forced - Delayed | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Winter | 119 | 17 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 800-Miscellaneous
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1032.4999 | 210 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 605 | 110 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 37.9667 | 17 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 15.7333 | 16 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 147.25 | 31 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 982.6666 | 55 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.5 | 35 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.9166 | 151 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1745.333 | 440 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.8648 | 113.23 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7962.75 | 135 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.7333 | 172 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.2 | 48 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 324 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 751.68 | 234.9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1575 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8287.5 | 850 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217.5 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1249.5 | 147 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2725.6664 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1559.9999 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1793.9999 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2070.6165 | 283 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184.8 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2885.85 | 363 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 960.05 | 211 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5810.25 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5049 | 255 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24050 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.2185 | 48.31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 453.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1928.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.8333 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 226.0965 | 38.43 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 492.9666 | 46 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1125.2999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1225.4664 | 364 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1548.5999 | 261 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2175.4996 | 570 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2299.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2899.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.6667 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.3333 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121.3333 | 112 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1057.4998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6364.05 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348.4 | 134 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3360 | 480 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2184 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 471.5 | 82 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4484.4 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4414.3331 | 380 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21526.7023 | 175.18 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4113.2 | 728 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6891.7328 | 728 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 246.6667 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 490 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2384.9 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4380.9333 | 232 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.3332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.5 | 250 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 579.8332 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1347.9665 | 371 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2566.6662 | 700 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8436.9998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 411.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 628.5666 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1347.9998 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 54.7167 | 18.76 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.0691 | 85.91 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 275 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3060.5833 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.7666 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3721.25 | 229 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 240 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10699.2166 | 299 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.5 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.9999 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 356.5332 | 191 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9960.4999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 420 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1125.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1702.652 | 30.66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4422 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 0.572 | 4.29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3135 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1749 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 210 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1066.6666 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2564.1 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.6666 | 46 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 644.8333 | 106 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 395.2 | 76 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7612.8 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1023.4665 | 202 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 935885.4664 | 824 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.5 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17451.5 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 469.7 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1600 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.65 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154 | 140 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.14 | 146.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232.6719 | 158.64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 284.6 | 142.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2942.4998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6696.6665 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.3 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 924.6666 | 95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1029.1665 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1851.1666 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2505.0666 | 112 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3859.5 | 498 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4064 | 508 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5318.4998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 212.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 223.8833 | 101 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 610.9333 | 116 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 937.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 974.5666 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 591.1 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 314.4999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5796.5166 | 293 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1013427.0664 | 836 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3209.2498 | 495 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2382.1 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 756 | 252 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2061.8 | 31.72 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.3333 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.6666 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2485.9999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3240 | 540 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3565.3 | 202 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 580.9997 | 498 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1446.6665 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1682.9999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3032.9999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.6665 | 428 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.1667 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 654.75 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1885.7498 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2199.9998 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3814.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10625 | 850 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 280 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 594.5 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 622.7999 | 216 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1313 | 101 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1591.2499 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4080 | 510 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2746.016 | 95.68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 759.055 | 82.06 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1488 | 248 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2040 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3336 | 139 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 490.9666 | 103 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10743.3 | 414 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5742.6662 | 730 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2225.0664 | 448 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3471.5 | 530 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4094.8 | 232 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5999.9998 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.25 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1832.1333 | 151 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 297.6999 | 78 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 723.3333 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 795 | 530 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1231.8331 | 389 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3933.333 | 500 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 397.0332 | 277 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 483.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 577.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 816.9998 | 285 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10638.6 | 298 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5989.5 | 363 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10722.3333 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 654.7497 | 405 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 314.25 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 440.8498 | 264.51 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 35.4 | 17.7 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 650-Fluidized Bed
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330 | 100 | 1 | 1 | 0040-Coal elevators | U1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6370.3331 | 580 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 153 | 60 | 1 | 1 | 0050-Coal storage fires | D2-Forced - Delayed | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4789.9998 | 600 | 1 | 1 | 0050-Coal storage fires | U1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4779.9996 | 600 | 1 | 1 | 0050-Coal storage fires | U1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 449.25 | 45 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2496.6665 | 214 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5886.75 | 235 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1080 | 270 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1160 | 290 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 10.8333 | 10 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 392.5 | 157 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1067.5 | 305 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 965.0666 | 154 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1303.8666 | 254 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414.5 | 30 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 967.6333 | 154 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4320.7666 | 338 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5184 | 216 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.0833 | 5 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1745.3332 | 280 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 675 | 180 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1147 | 310 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135.9999 | 96 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4774.75 | 355 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.6666 | 113 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1458.3332 | 250 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567.3332 | 230 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5079.1665 | 530 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136 | 120 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 311.9998 | 360 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 686.1666 | 230 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2339.3331 | 290 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 278 | 139 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83 | 60 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 685.3333 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 706.9999 | 420 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1085.9999 | 180 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.8 | 96 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 7457.5 | 95 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 20.3333 | 4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 116.8 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 13.224 | 5.22 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 86.5167 | 29 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 117.3333 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 104.1667 | 25 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 129.6 | 32 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 61.2333 | 22 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 67.5833 | 5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 77.5667 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 86.9 | 6 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 136.5 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 98.6666 | 40 | 1 | 1 | 0080-Stackers/reclaimers | U2-Forced - Delayed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 395.3333 | 40 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 191.25 | 17 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18.2 | 12 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 285.1333 | 26 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 70.8333 | 34 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 111.5333 | 28 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 13.3333 | 10 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 8.2 | 6 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 37 | 20 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 41.6 | 24 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 134 | 26.8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 173.8 | 15.8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 139 | 27.8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.9999 | 270 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 230 | 50 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | U1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 359.9999 | 270 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.9999 | 270 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66714.4828 | 839 | 1 | 1 | 0085-Bunker feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3935.9498 | 264.75 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87 | 87 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.6666 | 80 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5194 | 392 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53004.2498 | 705 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 355994.3331 | 580 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 368 | 80 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1088.8583 | 218.5 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 208 | 120 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 521.1666 | 106 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 831.1706 | 127.22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 911.7432 | 127.22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 367.5 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 436.1716 | 49.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.3167 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.6833 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.45 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 133.1667 | 47 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 661.3333 | 64 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1231.25 | 125 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 465.8 | 51 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 817.7 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 600.6666 | 170 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.8666 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 834.35 | 123 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 512.6332 | 182 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16.5 | 66 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.0833 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 663.9999 | 96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.849 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.6 | 36 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.5 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 325.95 | 123 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 355.2 | 96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1281.8666 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 92.4833 | 31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 241.5833 | 65 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66 | 66 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1065 | 426 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.45 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 120 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 812.7999 | 96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.4333 | 59 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118 | 120 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219.9499 | 159 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 870.9999 | 78 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 56 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 609 | 58 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3174.9999 | 300 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.9857 | 5.18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.1 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 506.6666 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 44.5833 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.8667 | 11 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 303.4 | 41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.3333 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 177.9166 | 61 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 309.3333 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.0667 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.5 | 86 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 836.7999 | 96 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2747.4 | 76 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1002.5 | 401 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.75 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5.3833 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76 | 76 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.7 | 51 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 13.3333 | 10 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 163.8 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 110.4 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 129.8 | 11.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 207 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 214.2 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 499.8 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 616.4 | 26.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 121.5 | 24.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 44 | 8.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 50.4 | 16.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 59 | 11.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 131.6 | 18.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 63.2 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 71.2 | 17.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 96.6 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 63.2 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 283.4 | 21.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 56.4 | 18.8 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 499.9367 | 27.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 62.0533 | 20.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 71.4 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 81.5 | 16.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 85.8 | 14.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 395.7283 | 28.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 262.2 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.2 | 27.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 118.8 | 19.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 47.2 | 11.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 99 | 19.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 55.2 | 13.8 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 70.4 | 8.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 23.2 | 5.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 32 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 112.4867 | 18.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 115.2 | 28.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 309.4 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 354 | 11.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 118.8 | 19.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 47.4 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 58.8 | 9.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 62.4 | 20.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 100.8 | 16.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 69 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 166.6 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 297 | 19.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 414 | 13.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 830.8 | 26.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 15.2 | 3.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 53.4 | 17.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 126.4 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 168 | 16.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 425.645 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 41.4 | 13.8 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 63.2 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 141.9367 | 15.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 184.8 | 16.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 51.2 | 12.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 162 | 10.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 33.9 | 11.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 104 | 20.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 213 | 21.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 380.4033 | 23.8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.6667 | 20 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3156.92 | 18.68 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1788 | 40 | 1 | 1 | 0100-Bunker gates | U2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155 | 31 | 1 | 1 | 0100-Bunker gates | D2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 863.3333 | 40 | 1 | 1 | 0100-Bunker gates | U2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2414.6666 | 40 | 1 | 1 | 0100-Bunker gates | U1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 7.9333 | 17 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1096 | 48 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 940.565 | 31.3 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 800-Miscellaneous
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2424 | 202 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 82.1667 | 29 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 273.3333 | 50 | 1 | 1 | 0107-Screen (prior to bunkers) | U1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 93.3333 | 35 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.5 | 185 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.125 | 29.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.6667 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.9996 | 552 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.4 | 84 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 695.25 | 309 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 728.75 | 75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 881.9998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 309.7365 | 199.83 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1219.4998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1378.66 | 47.54 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 507.9165 | 265 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 848.3894 | 316.17 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1261.148 | 122.64 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8442 | 422.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10667.4666 | 218 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9016 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190 | 380 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3878.3332 | 325 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1223.9999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6649.1999 | 108 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 275 | 110 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.6666 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1535.1953 | 554.89 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1868.75 | 325 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2638.035 | 586.23 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 532.1666 | 155 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 42.0567 | 13.64 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 274.4833 | 43 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1.4183 | 2.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 16.76 | 4.19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 68.24 | 8.53 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1.8333 | 2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.0167 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 17.2 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 50.8867 | 3.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9.975 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 4 | 4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 4.32 | 2.16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 29.2 | 14.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 4.4083 | 2.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 13.41 | 1.49 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 18.34 | 2.62 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2.99 | 1.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.375 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 7.8117 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 4.62 | 3.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 6.9 | 2.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 16.35 | 10.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 6.8 | 1.36 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.8933 | 5.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 16.6 | 8.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 54.6667 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 19.355 | 4.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 46.6933 | 6.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 48.12 | 8.02 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 5.25 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 409.2 | 9.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 13.74 | 4.58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 34.1666 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 15.3 | 9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1.505 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 72.1483 | 7.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 235.79 | 12.41 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 23.04 | 11.52 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 0.54167 | 1.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1.65 | 3.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 8.2967 | 3.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 18.2 | 3.64 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 44.37 | 4.93 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 5.84 | 2.92 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.9 | 3.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3.98 | 1.99 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 5 | 5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2718.9733 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 8632.2249 | 224.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1.47 | 1.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 5.3 | 5.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 7.52 | 1.88 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 11.36 | 2.84 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 58.7667 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 159.5 | 7.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9.03 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 18.06 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 31.98 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 10 | 10 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 16.24 | 1.16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 31 | 15.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 23 | 11.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2.2867 | 2.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 3.45 | 2.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 38.8 | 7.76 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1.4083 | 1.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 38.8133 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 40.635 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 67.77 | 7.53 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 212.5 | 12.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 23.04 | 5.76 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 8.9217 | 5.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 21.24 | 2.36 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 30.66 | 4.38 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 7.525 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 11.445 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 16.12 | 6.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 26.65 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 4.095 | 6.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 4.96 | 2.48 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 21.2917 | 7.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 28.0167 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1460.1 | 9.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 819.4333 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 168.85 | 33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 170.3 | 39 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 4002.0833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 6.6 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 8.2167 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7 | 30 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7.3667 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 170.8333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 6.3333 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 137.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 8.2666 | 31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 10.3333 | 31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 10.7333 | 23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 16.5 | 33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11.3333 | 20 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 13.6 | 34 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 5 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 311.6667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 166.95 | 27 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6.9 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 105.8333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 11.6667 | 35 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 275 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 13.0666 | 28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6.5167 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 8.7833 | 31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 11.55 | 33 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 17.5666 | 31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 392.0833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 24.2833 | 31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 4 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 8 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.4 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.6 | 3.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 58.4 | 7.3 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10 | 5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.4 | 5.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 22.2 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 5.1 | 5.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.4 | 6.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 212 | 21.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.7 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10 | 5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 14 | 3.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 102.4 | 12.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 15 | 5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7.8 | 7.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.1 | 5.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.4 | 5.4 | 2 | 2 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 11.1 | 3.7 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 15.5 | 15.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 54 | 13.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 20.4 | 6.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 90.1 | 17 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 96.25 | 33 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 292.05 | 33 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 249.6666 | 28 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 36.4 | 26 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D2-Forced - Delayed | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2.78 | 2.78 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 24.8 | 24 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 34.5167 | 9.5 | 1 | 1 | 0116-Solid fuel feeder motors | D2-Forced - Delayed | 650-Fluidized Bed
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 131.5 | 13.15 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 7.68 | 3.84 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 909.448 | 37.92 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 11.16 | 5.58 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 2.25 | 2.25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 14.25 | 4.75 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 11.34 | 3.78 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 129.2 | 7.6 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 334.9998 | 300 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 20.08 | 5.02 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 74.04 | 6.17 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 3.61 | 3.61 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 4.3 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 16.86 | 5.62 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 50.9167 | 13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 800 | Miscellaneous | WECC | Winter | 212.8 | 19 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 58.6667 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 78.8667 | 14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Winter | 0 | 0 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 22.6667 | 17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2020 | Other | BM | 800 | Miscellaneous | WECC | Winter | 180.5 | 19 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 39.1667 | 10 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 512.82 | 12.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1967.25 | 183 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 881.9998 | 270 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.4998 | 270 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.4 | 36.3 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1240.3666 | 117.2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.4 | 31.8 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296 | 296 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 601.6664 | 361 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0139 | Sorbent handling drying equipment | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 352.5999 | 123 | 1 | 1 | 0139-Sorbent handling drying equipment | D1-Forced - Immediate | 650-Fluidized Bed
0139 | Sorbent handling drying equipment | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 432.5499 | 123 | 1 | 1 | 0139-Sorbent handling drying equipment | D1-Forced - Immediate | 650-Fluidized Bed
0162 | Bed material conveyors A | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 57.3467 | 6.8 | 1 | 1 | 0162-Bed material conveyors A | D1-Forced - Immediate | 650-Fluidized Bed
0162 | Bed material conveyors A | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 291.72 | 5.72 | 1 | 1 | 0162-Bed material conveyors A | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 990.605 | 9.3 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 550.87 | 9.3 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 15.5 | 31 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 13.6667 | 41 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 18.6667 | 14 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 254.4 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 517.5 | 90 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2525.8333 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4975.8333 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 425.6 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81.3167 | 41 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1527.9999 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 740 | 48 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4513.6933 | 27.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 359.7333 | 76 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.8333 | 39.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276.6833 | 13 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 428.7999 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4604.6 | 64.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 366.6666 | 100 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 60 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.64 | 29.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1049.5833 | 55 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10484.1 | 59.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5890.95 | 49.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.75 | 79 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 476.4 | 79.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4182.4667 | 34.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.8 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2312 | 54.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128 | 96 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 928.86 | 27.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2325.6 | 54.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2656.9733 | 40.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 710 | 75 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.3332 | 200 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106.6667 | 16 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126.6664 | 400 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340 | 400 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 55.4166 | 175 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 331.5 | 170 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123.5482 | 322.3 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 583.3333 | 100 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 162.9166 | 115 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 201.25 | 175 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2173.5 | 90 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 495 | 300 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 863.3331 | 700 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 87.5 | 250 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 942.5 | 650 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 757.1832 | 251 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2462.5 | 250 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.832 | 66.96 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 375.0665 | 232 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.55 | 71 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 29.1666 | 175 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2492.4999 | 150 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184.1666 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1584 | 110 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56.25 | 125 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 220.4166 | 115 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 375 | 250 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 378 | 135 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.6914 | 164.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 44.2865 | 204.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.45 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.3083 | 33.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.3333 | 166 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.6 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 118.1266 | 244.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 136.7333 | 234.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.8333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.8333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144.3593 | 109.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.8666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.4975 | 228.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 194.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 238.3065 | 234.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271.7216 | 125.41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 277.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408.8 | 20.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429.9533 | 234.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 442.4058 | 178.15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450.85 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 462 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 678.3999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1015.7699 | 88.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1398.7912 | 230.57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1486.25 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1668.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2925 | 390 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4534.75 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4648.1331 | 284 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.0666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.1 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.5333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.2 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100.32 | 26.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.932 | 134.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158.848 | 186.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 184.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.9166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 318.2667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 625.1 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 643.5 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 679.9333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1321.4166 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1675 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2125 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2186.6 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2832 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3655 | 107.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.118 | 15.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.375 | 148.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.9976 | 43.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.3023 | 37.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.85 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.3 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128.325 | 130.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.25 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 217.8264 | 384.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220.8332 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 293.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 302.1666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360.9666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 431.8 | 38.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 499 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 864 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1440.2666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1.8783 | 16.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.185 | 45.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.2333 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.8999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.3666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.0649 | 89.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 249.9 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 313.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.3678 | 29.87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 127.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.573 | 11.21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 68.2 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.5 | 73.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 93.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 125 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 131.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 282.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 681.8833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3262.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640.2573 | 50.68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.5833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 193.2 | 72 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 238 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 392.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 641 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 423.85 | 173 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 433.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2009.3332 | 137 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | U2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5283 | 30.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 22 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.1166 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.9666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.3333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.25 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 71.1 | 284.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.95 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.0833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 185.0596 | 584.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 210.96 | 234.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 283.5731 | 654.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 339.3132 | 264.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360.661 | 15.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370.4166 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 477 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 661.3329 | 620 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 722.6932 | 264.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 837.3774 | 164.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 968.0257 | 163.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1525.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2154.3 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9859.2015 | 265.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.255 | 29.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.6276 | 55.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.3333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.1999 | 154.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.0666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 126.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 174.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325.04 | 47.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 375.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 393.9 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 473.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 770.8332 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 951.5582 | 128.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2853.55 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.9983 | 43.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.7333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.01 | 13.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.35 | 148.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 71.0963 | 609.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115.9 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144.105 | 73.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 154.9999 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.1067 | 34.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 400.6333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 417 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 433.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 470.6585 | 91.39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 503.28 | 419.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 533.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 648.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 758.333 | 455 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 758.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 971.8316 | 86.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 978.0333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 982.4 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1425 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1858.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2252.2666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3020.4333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3120 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3794.7 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3921.08 | 146.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.85 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.4 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 130.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.3833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 659.4765 | 158.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 142.9333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 414 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 756.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2870.35 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4920.4166 | 245 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.4 | 66 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 421.2 | 216 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 444.85 | 93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 561.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 997.5 | 175 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.4333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 255.2333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.2499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 134.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 299.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189.75 | 33 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 952.233 | 539 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1059.75 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1507.2 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9328.6585 | 814.73 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2382.195 | 437.1 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.7999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64.5999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 122.7666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 138.5362 | 639.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 160.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 173.8 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 178.1332 | 534.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 200.2832 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244.64 | 244.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.5 | 450 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 270.4 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.0333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 359.8333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 485 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 493.0963 | 68.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 506.7665 | 264.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1032 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1052.7 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1391.7091 | 364.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1470 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1500.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1530 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1718.5833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1731.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.211 | 12.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.9333 | 86.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.5 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.998 | 303.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.4033 | 35.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 338.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 420 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 487.3333 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 498.7999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 616.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 675.925 | 142.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1061 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1133.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1359 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1445.5 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2160 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2777.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4083.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9600 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67731.9331 | 326 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.25 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.5416 | 77.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.5 | 118.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.75 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 67.8 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77.8666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90.0333 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.9666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 354.6666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360.3999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 557 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 596.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 606.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 626.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 691.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 794 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1032.5 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1638 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3244.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15009.8666 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.9 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.221 | 52.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.0666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 495.7163 | 53.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.2 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.1333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 155.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.183 | 12.33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 478.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 523.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 136.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 242.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 317.1999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 355.8331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1202.6665 | 410 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2803.3331 | 290 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 413.4 | 156 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6799.0832 | 415 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 600.3 | 174 | 1 | 1 | 0250-Pulverizer feeders | U2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.6826 | 73.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.5333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.8166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 101.76 | 254.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.9 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.65 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143.25 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 221.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 267.12 | 254.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 301.3 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451.04 | 140.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 623.3833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 793.5664 | 358 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 894.3528 | 64.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1330 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1485.9 | 114.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1605.1499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1990.9501 | 162.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2223.1405 | 144.83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2301.9791 | 134.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3150 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11069.652 | 394.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11285.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.2998 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.1666 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.5 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.7999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.4998 | 279 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.95 | 125.94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132.9833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.15 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 239.7333 | 179.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 292.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 345.6666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.144 | 138.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 591.0666 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1084.4166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1244.6 | 88.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1269.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2475 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3248 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3779.1 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5062.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.85 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.3 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 183.3332 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 261.76 | 654.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 303.45 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 375.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 436.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 442.25 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 478.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 560.082 | 164.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 697.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 793.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 794.8833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1015.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1403.1697 | 414.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1993.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2568.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5113.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7397.75 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10031 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.1333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1241.6167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1612.9 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.8 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.0666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 197.3333 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 276.051 | 49.59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 329.6333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.0093 | 22.12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 52.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.8166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.9 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.5833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.3375 | 63.47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376 | 47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 167.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 521.0833 | 169 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14739.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 339.9666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28443.9995 | 780 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1838.8333 | 85 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2783.45 | 311 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.9333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.0625 | 74.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.151 | 71.34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.5666 | 311 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 100.32 | 334.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.9 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 123.1166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137.5833 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.8 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.6666 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 265 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288.75 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 453.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 565.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 619.2 | 172 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 628.65 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 664.7 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 909.4773 | 114.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 933.684 | 214.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1010.3439 | 164.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1359 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1577.3332 | 260 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2000.2499 | 189 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2541.408 | 264.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2893.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.4333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.1435 | 35.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125.01 | 41.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 126.5832 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.1665 | 229.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.0166 | 142.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 208.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 301.3166 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 303.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 402.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 565 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 615 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 740.25 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 840 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1168 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1256.28 | 136.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1598.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1695.792 | 164.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2961 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3195.8333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4401.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.2499 | 97.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.7398 | 121.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.25 | 100.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.6666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.9 | 212.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.5316 | 94.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159.25 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 251.6 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 341.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 426.072 | 207.84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.1467 | 36.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 589.8666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 647.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 670 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 684 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1262.9833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1684 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9850.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.225 | 19.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 97.15 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102.6666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118.45 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.6207 | 14.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 260.4 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 770.4 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.85 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 437.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 602.25 | 219 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245 | 98 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.2 | 72 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 208.25 | 105 | 1 | 2 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 216.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 340 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 446.2499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 448.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 854.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 244.55 | 67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 760.4666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192.8833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 345.15 | 59 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 410.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 501.5 | 59 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16501 | 290 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.85 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.104 | 26.38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 22.2798 | 668.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.3333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.5666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.5832 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.9355 | 15.47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.6666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.05 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.4974 | 343.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 203.2 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 217.25 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.5 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 274.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 289.4166 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 297 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.5333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 326.0932 | 264.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.5373 | 14.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 348.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 421.2 | 156 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.2666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 463.1 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 495.4165 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 496.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 497.9532 | 264.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720.1666 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 787.0132 | 214.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1087.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1184 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1234.9166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1456.9999 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1641.8031 | 289.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9835.3556 | 394.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18227 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.26666 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.1667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.639 | 24.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.6975 | 26.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.9999 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.1166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.3 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.5 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154.1 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.275 | 60.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.162 | 124.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186.3 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 202.1 | 202.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 218.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 413.1666 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 497.9856 | 105.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 572.6233 | 17.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1120 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1125 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1416.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2217.1166 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3091.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5171.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.994 | 45.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.4655 | 45.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.75 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.9995 | 308.57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.1833 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 175.32 | 584.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176.4166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 299.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 411.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 618.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 787.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1205.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1775 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2024.1 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2847 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2851.3833 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2880 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5184 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7390.76 | 146.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8715.2 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 11 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 237.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 238.4999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2289.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88.413 | 68.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.7 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 198.8 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1012.55 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2758.8166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 150 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 8.125 | 2.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156 | 2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1838.34 | 102.13 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 172.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 225 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 442.8 | 82 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 735.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.4333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 530.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1364.25 | 255 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7692 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 661.5862 | 684.4 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 839.9498 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5385.0998 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.15 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.4666 | 127 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.95 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.0325 | 37.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.8165 | 244.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.9499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.0515 | 63.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 132.8265 | 234.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.4666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.8332 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 175.8 | 234.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.3666 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.2 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 235.1833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 294.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 375 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 442 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 452.6958 | 65.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 508.3666 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 526.75 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 545.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 739.4998 | 306 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 905.746 | 364.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1081.35 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1302.96 | 162.87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1776.5 | 104.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.75 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2833 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.3 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.998 | 126.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.976 | 173.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.55 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 105 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.836 | 94.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 127.7099 | 139.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.3333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 228 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.5833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.7833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 343.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 392 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 465 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 624 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 651 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 655.4166 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 770 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1283.4 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1337 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2192.575 | 113.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2265.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2777.8403 | 124.66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5347.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.677 | 2.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.0333 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.9645 | 29.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55 | 110 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.925 | 148.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 84.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109.1714 | 89.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 120.75 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.9958 | 261.42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.8333 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 313.3 | 125.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 333 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 335.907 | 70.47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 356.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 378 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 473.1332 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 481.3332 | 361 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 561 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 566.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 621.2192 | 35.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 673.1998 | 297 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 828.857 | 59.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 846.1332 | 534.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1948.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3842 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12795 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.4 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.75 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 199.5 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 318.4666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 339.95 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1099.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 168.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 492.2 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.3333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 513.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 807.75 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 77.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158.3332 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 361.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 667.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 746.4166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 783.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.4 | 42 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.7 | 39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3696 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.8333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.4666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.4 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.3 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.6332 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 98.3466 | 184.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.2665 | 264.64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 149.2399 | 344.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492.9 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 508.8333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 562.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 579.3839 | 167.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665.1666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840.9653 | 130.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 856.34 | 364.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2482 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2763.11 | 394.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3443.561 | 121.11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.2783 | 43.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.9987 | 36.92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.405 | 29.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 60.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.6333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.7333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.1667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.2667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.2666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.3332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154 | 123.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.6666 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.75 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 247.095 | 164.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 348.3333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 361.35 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 394 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 408.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 507.1666 | 179 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 598.5 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 624 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 637.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 816.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1189.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2146.2 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2558.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3245.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6716.4165 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.2588 | 5.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.1833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 40.15 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.862 | 125.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.9596 | 674.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.6 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 86.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 181.6558 | 114.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 204.8532 | 534.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.1666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 348 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 396.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 554.212 | 41.88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 560.3865 | 634.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 660.3 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 740.7666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 956.45 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 956.6499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3393.75 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.0667 | 21.05 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 49.9999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.9833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 103.95 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.8 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 250.5816 | 59.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 940.1 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88.35 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 118.15 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 162.9333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1332.25 | 18.25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2324.102 | 17.88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.1 | 22.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 255.75 | 31 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.7833 | 41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 374 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 377 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 387.9166 | 133 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 425.25 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 417.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42 | 210 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.5333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 394.8333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1276.5 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1889.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5986.5 | 614 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19944.7665 | 614 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 628.833 | 539 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4451.2 | 832 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37786.6658 | 1300 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92419.9998 | 600 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4904.8662 | 684.4 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 26 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 28.8 | 14.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 61.25 | 17.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2578.8667 | 38.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2335.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 294 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3504 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 120 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 336 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 828 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 876 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 390 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 669.1666 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 716.8333 | 115 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1728 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 320.8333 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 400.1666 | 98 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 75 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.6666 | 82 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.7333 | 119 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9362.835 | 244.78 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.705 | 56.78 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3906 | 126 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 155.596 | 55.57 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 205.8333 | 190 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 128.3332 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 373.6665 | 190 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 186.6666 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.5167 | 47 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6000 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71483.5 | 634 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 203 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53.8583 | 28.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.1667 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66640 | 850 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 34.1833 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 186.9 | 18 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.5 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 292.5 | 75 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.0016 | 92.77 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 632 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1598.3333 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2143.4166 | 89 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 434.5 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.3792 | 19.25 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15110.85 | 153.8 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.4666 | 56 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1464.8533 | 141.76 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 434.145 | 28.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 635 | 75 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.1333 | 56 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.7253 | 35.08 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.8665 | 256 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.952 | 12.44 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 161 | 35 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.4166 | 127 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.205 | 33.1 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93 | 31 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214.7664 | 379 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3153.76 | 171.4 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 60 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 555.2866 | 65.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2815.1665 | 190 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.4733 | 65.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.3333 | 80 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.1933 | 123.76 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480.6833 | 151 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1496 | 680 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4980 | 498 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9752.5 | 83 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 244 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 905.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1078.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1380.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10750 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210.8 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2731.9999 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4012.6663 | 520 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 232 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 300.5 | 30 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14313.1664 | 785 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1913.347 | 466.67 | 1 | 1 | 0260-Primary air fan | U3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4855.5 | 83 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15635.7 | 54 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 158.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195.65 | 39 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1202.6666 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2117.4998 | 330 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3167.8332 | 415 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18838.833 | 545 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.64 | 19.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.8333 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 343.8 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 514.4999 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 705 | 141 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1000 | 125 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 922.5 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83 | 20.75 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 436.3333 | 220 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7019.6328 | 839 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4526.6666 | 112 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6841.9996 | 660 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 336.833 | 470 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 359.2583 | 226.9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 471.9998 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1950.9665 | 214 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3299.9998 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 530.7 | 18.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6009.8999 | 234 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 583.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 497.13 | 136.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 693.8332 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28886.6665 | 560 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.3 | 87 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1680 | 420 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.97 | 13.69 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 392.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.1665 | 530 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53517.083 | 515 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 200.5332 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10069.3331 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12390 | 295 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25530 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75267.25 | 515 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4073.3332 | 520 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 873.8 | 514 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7505.3332 | 520 | 1 | 1 | 0260-Primary air fan | SF-Startup Failure | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1347.5332 | 493 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 324.2666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 587.9998 | 630 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.45 | 127 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 993.6665 | 220 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1704.5332 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1320 | 55 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 147.5 | 150 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 677.1666 | 170 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6546.1333 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.8696 | 116.99 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 697.6667 | 7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227.0833 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 449.1667 | 50 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 516.2666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2939.3333 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 301.2016 | 142.3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 498.3332 | 260 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 916.5833 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1199 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2727.592 | 514.64 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 773.2999 | 111 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 800 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 818.6333 | 82 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2401.2 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.03 | 12.67 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.5 | 10 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 651.1 | 102 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 453.9733 | 10.64 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 6.05 | 3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 339.3 | 18 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 12394.65 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 260.3999 | 126 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2328.8328 | 785 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.3333 | 40 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 966.6666 | 80 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1547.9996 | 540 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1650 | 300 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.7628 | 16.81 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 732.7666 | 89 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.89 | 5.97 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 72 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260 | 400 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1399 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 710.0332 | 179 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.25 | 15 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2468.6664 | 460 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1260.8333 | 89 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9628.5 | 655 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3777.3499 | 93 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 437.8 | 33 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1240 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9450 | 108 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.9213 | 55.63 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 648.0166 | 59 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 809.4666 | 104 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 615.9997 | 420 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9293.7499 | 375 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13959.8 | 223 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2712.5 | 15 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6246.1666 | 55 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 114807.183 | 437 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 177.4666 | 121 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.4833 | 41 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595 | 119 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.75 | 15 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 80 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5204.9997 | 900 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.5 | 230 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 431.1999 | 168 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 297.5 | 150 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 105 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 2676.1 | 382.3 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5530 | 158 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32046.6287 | 201.53 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 248.1999 | 219 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 280.8 | 351 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.3333 | 100 | 2 | 2 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16328.0833 | 115 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1314.9 | 18 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 650-Fluidized Bed
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391 | 170 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2766.4833 | 127 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 71402.2165 | 369.8 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42 | 21 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 15 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2574.2 | 422 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.99 | 29.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1767 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3790 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 55 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.5 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.6667 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 90 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 289.4999 | 90 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 490.8333 | 190 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7093 | 820 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.79 | 58.79 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.8666 | 127 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 505.7325 | 66.69 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.9166 | 185 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 212 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220.5 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 972 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 307.3565 | 130.79 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 20 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1005.7998 | 564 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.802 | 39.64 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.75 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99 | 55 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 284.6666 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1953.98 | 279.14 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 80 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.7833 | 71 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330.9166 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 664.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1474.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.75 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6286 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.0833 | 65 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95.8333 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1436.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1847.8499 | 87.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 380 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 283.6666 | 230 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 638.7332 | 143 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5186.6667 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20241.8333 | 61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 628.05 | 159 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 701.1 | 27 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 828 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1032.5333 | 64 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2507.0165 | 419 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2282.5833 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.75 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 371.7 | 9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 511.7332 | 152 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 666.6665 | 250 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.8666 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237 | 79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1229 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4912.8166 | 281 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.9333 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.9167 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 279.8333 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 675 | 450 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.4999 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 978.75 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.6666 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.5 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1340.5 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4181 | 148 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1485.95 | 113 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36414.0333 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47.15 | 41 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.0833 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 331.5 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 657.3332 | 170 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5491.4996 | 630 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.5 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429.5666 | 263 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 14084.3333 | 31 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1389.2 | 151 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2232.9999 | 210 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 142.5667 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.0667 | 32 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 410.85 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 646 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7873 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 583.9166 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1821.05 | 121 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345 | 138 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32328.9999 | 132 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.024 | 228.64 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.1998 | 353.25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 576 | 240 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 969 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 895.1666 | 131 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1381.5333 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 283.3333 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156.15 | 10.41 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.5 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 744 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 920.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1469.5786 | 35.44 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.2333 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.1 | 61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5686 | 144.79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.4666 | 58 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1351 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261.825 | 104.73 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 262.8 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9522.5 | 650 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3568.0666 | 179 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.5833 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 223.8666 | 92 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 387 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.8333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 948 | 144 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1007.3667 | 47 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 416 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.6 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4995.8332 | 550 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7981.3331 | 820 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 419.6833 | 169 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 60.3478 | 452.61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.9666 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 597.0226 | 617.61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 784 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1256.4955 | 562.61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 580 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 10532.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39628.7333 | 89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1781.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 209 | 190 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 443 | 443 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.1333 | 44 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374.4 | 117 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2392 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10575.9999 | 192 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 519.3331 | 380 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6712.5 | 179 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.4 | 96 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.0666 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1378.5833 | 71 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339.3 | 117 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 350 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182.85 | 69 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 777.5 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 336.6665 | 202 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144.6666 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.6666 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 630 | 28 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7600 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.5333 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 723 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1609.6666 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160 | 160 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101 | 101 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.9999 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6225 | 150 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44905.5 | 153 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.1333 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10783.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 295 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1199.6666 | 122 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 218.4 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 273.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 559 | 172 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1457.8666 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 185.7333 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660.7332 | 212 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 539.8331 | 395 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1485 | 495 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195.5 | 17 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.6667 | 16 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 619.1166 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1204.1292 | 142.22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107679 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 610 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1408.1666 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2109.8 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17202.5 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 309.75 | 59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 564.8066 | 36.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 594 | 198 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 688.3332 | 236 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3061.24 | 36.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12580.4166 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.94 | 3.86 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 245 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 909.7833 | 247 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.1625 | 12.75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 482.65 | 197 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 615.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4862 | 221 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 367.4999 | 126 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1450.54 | 36.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1102.4 | 212 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6264 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.5 | 79 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 501.4166 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220.5 | 63 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 290.5 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381.5 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 488.8333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1721.7666 | 157 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2526.25 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.6166 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 279.3333 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 340 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 52.5 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 352.3333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.9677 | 15.61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 53.8332 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 478.2133 | 126.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 638.25 | 345 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 773.5 | 221 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3085.9999 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5185.4 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5342.9999 | 117 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2682.4499 | 81 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1277.8333 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 241 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1191.6666 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21.5833 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.6 | 72 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215.8332 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1323.6666 | 76 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4605 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7197.8666 | 64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1077.1499 | 387 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2791.2733 | 36.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6913.8166 | 59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 852.5 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1089 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123 | 61.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2053.3333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.5 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 164 | 16 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2100 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 609.7 | 67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 227.8 | 68 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 251.9999 | 135 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1839.9333 | 193 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.915 | 10.14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.05 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 296.6666 | 89 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10934 | 140 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16177.2 | 221 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 510.8666 | 79 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 761.9999 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163.1666 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1188.8333 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 602.95 | 93 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1295 | 70 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2900 | 400 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136.5 | 6 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1713.2266 | 36.4 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3806.22 | 86.9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 133.3333 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 70020.1833 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.0833 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.0667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.6 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189.9333 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 294 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 355.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 875.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 934.4665 | 214 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1067 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1547.5832 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1573.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2903.0416 | 96.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6868.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.0666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.25 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.5166 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.1666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.7333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 489.6 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 602.55 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 620 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1058.3333 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1066.55 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1479.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1988.0667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2010.6666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2723.9715 | 398.63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8131.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13487.552 | 55.68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21111 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.15 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 160 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315.0833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 736.6666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 762.0133 | 85.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 900.2333 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1349.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1374.75 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2835.4166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3215.9126 | 65.99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6762.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9268 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10712 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12105 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22209.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.9667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.8666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.3999 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 347.0666 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1467.7333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.0167 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.6666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 135.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 985 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.6 | 19.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2090.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1913.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63 | 9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1310.8226 | 89.68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 176.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 549.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 685.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1267.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1400 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2361.15 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3618.75 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4235 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.4167 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.3167 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.9667 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 680.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 715.1833 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2040 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2188.4666 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7709.35 | 131 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 954.1166 | 131 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4339.45 | 59 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10479.1663 | 625 | 1 | 1 | 0310-Pulverizer mills | SF-Startup Failure | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 444 | 555 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2508.3328 | 860 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.25 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.4999 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.45 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 260.3333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285.6333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 366.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.1998 | 294 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 924 | 330 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1080 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2502 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11604.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12583 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30819.4666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.3833 | 1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.5 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.3333 | 116.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 239.1633 | 91.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 373.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 441.7839 | 164.64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444.771 | 164.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 448.7755 | 212.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474 | 316 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 509.9499 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 784.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1227.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2237.0832 | 295 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3666.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3756.6666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4423.6666 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4699.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7354.9 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19452.5332 | 272 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20342.3 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.1 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.9999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.9167 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.4998 | 450 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140.4164 | 337 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.8999 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 799.3999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1164.5 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1617 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3116.4 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6181.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6645 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.1 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 296.8666 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 77 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 362.1 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 373.9416 | 97.55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.8213 | 134.32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 510 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2984.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.15 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.3333 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 387.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 414.3333 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 509.8333 | 133 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1958.4166 | 71 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.6 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.2 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.3167 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 554.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 400.05 | 127 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 400.4333 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 435 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 480 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 680.85 | 51 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 985.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2355.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5404.9166 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 80 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1604.2 | 52 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1688.5167 | 41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2207.7 | 223 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.0833 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.65 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 207.1 | 218 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 253.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 330.2 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 499 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 561.736 | 114.64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 722.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 750 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1878 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5025 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5376.6973 | 591.93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5508 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5681 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12876.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17241.95 | 319 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.9166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.7 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 83.6 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.5333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.1833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 341 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 602.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 679.0831 | 281 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 945 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 971.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1116 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1385.9999 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1583.9999 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2115.75 | 217 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2890.782 | 205.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6364.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17335.5 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.9167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44.8 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 220 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.8 | 189 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 383.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 642 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 725 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 943.356 | 49.52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1440 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.1 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.9 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5178.9666 | 251 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.085 | 12.06 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 85.707 | 48.06 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 177.1513 | 34.51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2889.6 | 33.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1674 | 108 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.8 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.5833 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.05 | 9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 168.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 174 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 216.5833 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 412.8 | 129 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1005.7333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1813.5667 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7066.5833 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.2333 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4208.7499 | 111 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.9333 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.9166 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 120.3333 | 190 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 541.0833 | 151 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 602.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9274.7 | 163 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19305.8 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4079.1833 | 67 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.4333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.3333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 132.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 209.4499 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 242.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 250 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 462.3333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.2253 | 39.16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 532.7332 | 262 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 823.5 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1059.1166 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1276 | 232 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1732.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2043.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2542.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4175.65 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4198.3333 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5720 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7198 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14712 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.25 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5333 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.7333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.9666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.8 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.8 | 184 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.4166 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 121.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 138.8333 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 258.85 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 275.6833 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.45 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 355.3332 | 164 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 377 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 393.3 | 171 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 544.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 641.3333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 656 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.4 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 977.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1327.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1900 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2032.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2792.9999 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2835 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18646.8 | 379 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.7999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.5 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.9999 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 152.1333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 174.6666 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 186.9 | 89 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200.5333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 284 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 610.5 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 686.3333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 701.4 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 747.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1982.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9900 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.3166 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.1 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.2 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 308 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 430 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120.75 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 990 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 976.0832 | 221 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1050 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1100 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.4827 | 162.77 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 660 | 44 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 845.55 | 9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 294.7666 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 847.3333 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1061.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1122.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1320.5833 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1729.8333 | 214 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2665.05 | 327 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3787.0333 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 735.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 915.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8207.9333 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 147.8165 | 181 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 251.1 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 355.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 681.75 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 806.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 841.5 | 153 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 923.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3741.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6508.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16591.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22297.9166 | 275 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.1 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.6 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 122.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200.2 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 494.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 886.5 | 197 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1487.9833 | 48.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1496.3333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4604 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4994.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5921.9333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.2 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.6 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 128.1 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 414.9346 | 163.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 420 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 539.6 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 607.05 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680.8332 | 430 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1840 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2070 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2076 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2542.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3139.2 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8676.2585 | 430.94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9350.0799 | 146.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 314.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1836.8 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 67.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1901.7167 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4214.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4442.6665 | 196 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96 | 32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 565 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1020 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1246.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2395.8166 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.2667 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.7666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 198.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 881.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1190 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1219 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1906.2333 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3749.3833 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10022 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1127.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3616.8833 | 41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 940.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21547.6665 | 635 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.6333 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.7 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.7666 | 24.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 310.0719 | 164.64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 517 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 684.45 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 775.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1280.275 | 41.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1443.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1722.7 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2108.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3157 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5281.2333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6049.5 | 185 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7006 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7443.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7912 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8026 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.75 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.3999 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279 | 186 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 290.0667 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.2 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 382.2667 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 383.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 463.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 508.3333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 584.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 590.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855.0833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1152.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1645 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1775 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6259.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 206.1833 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.8666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 672 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 887.1957 | 163.79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1127.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2254.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2295 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2308.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2758.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3241.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.2499 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 323.3 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5054.5997 | 762 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.6 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 438.3166 | 221 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1888.3 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.2 | 9.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 294.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 545.5733 | 32.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 868 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1186.1 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153 | 9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 621 | 69 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 209 | 44 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 289.5833 | 139 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 333.5 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 571.05 | 141 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 702.6666 | 136 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1215.65 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1253.7499 | 177 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5736.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.2333 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 161.25 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 296.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 494.4 | 32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 569.2166 | 49 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.8333 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 254 | 127 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 264.7332 | 209 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 456.4999 | 249 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 631.6832 | 251 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 912.45 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2010 | 67 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2769.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1052.3333 | 41 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1966.1165 | 223 | 1 | 1 | 0310-Pulverizer mills | SF-Startup Failure | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.333 | 440 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3245.3409 | 814.73 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.03 | 62.28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 223.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 331.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 498.4 | 356 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1096 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1284 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1352.6333 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1484.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2318.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4502.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4641.5666 | 163.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6008.75 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16378 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31038 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.2 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 55.5333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.6166 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.6665 | 380 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 193.4499 | 219 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.5666 | 86.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 580.1845 | 202.39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 606.7554 | 164.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 662.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1218.6 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1788 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2338.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3024 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3146.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4859.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31806 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.5 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.9997 | 414 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 300 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 351.9999 | 192 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 474.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.5843 | 88.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1212.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1738.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1986.3998 | 312 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8207.05 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.2333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.2333 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 75.4 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 912.6 | 156 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2394 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31005 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156.96 | 4.36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2208.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24.0333 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.25 | 195 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59 | 59 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102.55 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 374 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 796.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1691.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2115.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3080 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4813.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.3833 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.7167 | 47 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 609.5333 | 82 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 847.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2906.0166 | 131 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15673.8666 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2671.2 | 106 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.9332 | 248.9 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2108 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.6666 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105.3666 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.0666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 377.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 527.1 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 592.8 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 811.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3126.3165 | 267.97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3668 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4519.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5272.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6240.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11342.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.15 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 83.4 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.75 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.8332 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225.15 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 246.0332 | 242 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 284.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.7 | 274 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342.7526 | 169.96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 407 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419.5666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 484 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 548.812 | 124.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 692.2667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 922.5331 | 296 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3997.1666 | 290 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.8499 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.6 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211.4034 | 164.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236.4132 | 126.65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 374.1791 | 128.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 392.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 973.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1436.8833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1764 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4120 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4873 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17199.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3276.2833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.8333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.4 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.5333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 126.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 141.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 493.5666 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 232.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.0333 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.5666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 462 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 486.5333 | 178 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1142.5333 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1166.15 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8401.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.3667 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.1667 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.4 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.7499 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.5333 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.2 | 14 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 111 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 409.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 527.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 650 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1314.6666 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2244.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7216.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8982.7666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13542.0997 | 858 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 1176 | 196 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2256 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1150.3333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1371.6 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1525.5 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2448.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.9 | 87 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 492.0666 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1240.0015 | 237.7 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 203.5 | 111 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 529.1666 | 127 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1391.85 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.1333 | 11 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340.6 | 131 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 975 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76 | 76 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1944 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.2666 | 52 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 547.5166 | 91 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54978.3 | 127 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 637.5 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18651.5265 | 237.7 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1371.3333 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1968.64 | 76.8 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259.6666 | 82 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 305.25 | 99 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 580 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2147.4999 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2625 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.7 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.75 | 147 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2637.18 | 112.7 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.58 | 128.9 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280.5 | 30 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1019 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9560.8 | 19 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1353.6 | 144 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 455.775 | 88.5 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 761.4833 | 61 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1293.6 | 147 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2000.376 | 58.32 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.25 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 290.4 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6480 | 90 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3625 | 75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 656.8653 | 95.66 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 769.8332 | 155 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 790.2333 | 157 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1294.5332 | 292 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 543.6 | 151 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1041.9 | 151 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498 | 415 | 1 | 1 | 0315-Pulverizer mill coal level controls | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 138.6 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 676 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 518.75 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2968.6333 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1156.35 | 117 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469.375 | 75.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5604.0333 | 89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3927.5666 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.2666 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4584.6666 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 25 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1047 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.9666 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.7096 | 116.66 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 417.9999 | 228 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1077.0666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.6666 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 863.3332 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1908.95 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.9666 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.7 | 10.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8 | 12 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123.0666 | 104 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1782 | 180 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 517.9999 | 120 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.6667 | 5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8716.75 | 21 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 277 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2333.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.1666 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.1 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135.5333 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 227.2666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 353.3333 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 438.44 | 45.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.686 | 27.33 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.3333 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19183.35 | 381 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.75 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9020.6666 | 70 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11622.4999 | 150 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.28 | 24.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.0666 | 93.1 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3655.1666 | 130 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18554.1665 | 250 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1054 | 85 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.6 | 76 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 499.7 | 114 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 633.2666 | 92 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1050 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 895.9999 | 192 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2384.61 | 90.9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.4999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.1666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1364 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.4 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 135.85 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 420 | 126 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 170.3332 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 600 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.6667 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1063.2 | 72 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189 | 63 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1745.9999 | 216 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.3333 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 171.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 173.25 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 204.1666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 205 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 258.9166 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 277.5 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 318.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 595.4666 | 154 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 697.6666 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2323.9999 | 420 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.0833 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.0833 | 17 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.5 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2409.9999 | 300 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2419 | 205 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.2499 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 327.6 | 126 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 635.8666 | 251 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1180.6666 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 104.8333 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 252.45 | 51 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 472 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 560.2333 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1055.4 | 9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.6667 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.5 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1518.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.8333 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.4999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 657.3332 | 170 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 737.9999 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 404.25 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 411.3999 | 132 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 267.75 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 276 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 368.3 | 127 | 1 | 2 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3589.25 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6848.25 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 273 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 343.0833 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 344.1666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 350.4499 | 129 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 424 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1045 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.25 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 154.1 | 69 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1054.55 | 69 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1133.7499 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4799.5165 | 181 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 569.3333 | 112 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 769.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 793.5833 | 89 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1788.0832 | 215 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18613.1667 | 29 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 633.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 864.9999 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1195 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1487.5 | 175 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.6 | 86 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.4333 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 437.1666 | 215 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 211.6666 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249.6 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 804 | 144 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1116.6665 | 250 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 800.8 | 104 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.9166 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222.75 | 99 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 268.3333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 415.0833 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 90.8667 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 123.2 | 66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 292.1 | 127 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420.5 | 87 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 174.5333 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 380 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 465.75 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1145.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 462.5 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435.8666 | 56 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 312 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.95 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.2833 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 411.6 | 98 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.2166 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 342.9 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 280.4999 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1437.8832 | 253 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.5 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 475.8666 | 83 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4209.4346 | 144.82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209.55 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 227.4733 | 45.8 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 909.2 | 227.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.3 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.2 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.8166 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.6 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.4 | 72 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.1 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 347.1333 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 294.6666 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.8833 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.6 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2412.5499 | 183 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.7333 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199.1667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 239.1833 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.0166 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.3333 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 152.25 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.5333 | 127 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3972.1 | 66 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 244.8 | 51 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 833.6666 | 122 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.5 | 29 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 633.864 | 82.32 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 197.6 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 690 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 266.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 350 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 415 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 478.1667 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 556.9666 | 77 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 744.5332 | 128 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1067.9333 | 166 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.3333 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.9 | 27 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 345.1 | 119 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.8333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 158.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 204.9333 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.464 | 17.44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.4166 | 71 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1772.9833 | 91 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1811.3332 | 260 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.6333 | 77 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.2 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.6 | 131.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 257.54 | 65.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.9166 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.4166 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 744.9333 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 653.9166 | 133 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2216.6082 | 168.35 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 323.8266 | 65.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 307.5266 | 65.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 281.65 | 129 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391.7666 | 161 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 926.9332 | 158 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.25 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 196.4333 | 166 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 430.5 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1212 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1369.5 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 160.5333 | 112 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 492.9999 | 87 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 749.36 | 110.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 384.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 619.9166 | 173 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.8 | 27 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 760.2 | 84 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1669.2648 | 237.9 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.3333 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.5 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1284.8 | 146 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.0833 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 201.5 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 268.8 | 84 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 341.25 | 325 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 817.4 | 244 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 856.8177 | 45.86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 969.9999 | 300 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1028.5333 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5373.3329 | 650 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1369.5 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.4343 | 13.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.45 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 511.2333 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 888.25 | 187 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 194.3 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 795.4032 | 132.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1903.6498 | 333 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 396.6666 | 200 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 442.3999 | 168 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1067.2333 | 202 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1710 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.75 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2502 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1005 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 761.6 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.9333 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 358.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 719.5332 | 251 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.805 | 6.9 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 293.75 | 141 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9.5333 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 494.5 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 600.6 | 117 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.5 | 10 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.9 | 158 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345.6 | 128 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 381 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 555.3333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1027.2 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 710.0333 | 119 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 173.9 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 605.9332 | 149 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 132.75 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1175.3332 | 215 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.055 | 23.37 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351.9 | 153 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1431.1666 | 62 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.1161 | 40.87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14.5832 | 125 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.65 | 11 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 351.3666 | 127 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.3833 | 73 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 293.0666 | 157 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 332.8 | 128 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 601.8666 | 122 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.4666 | 68 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2440.5332 | 286 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 900 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1420 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 122.9166 | 125 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 140.6166 | 59 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.126 | 40.14 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.7 | 66 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 79.9999 | 75 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3181.86 | 96.42 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.65 | 57 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.425 | 23.37 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.25 | 181 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.5 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.3499 | 93 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 298.2 | 284 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 372 | 124 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1514.3333 | 70 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1353.7333 | 88 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1922.4 | 2.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 313.5 | 330 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | SF-Startup Failure | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 625.5 | 695 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1689.6 | 144 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 37479.1666 | 125 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1592.1 | 54 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24002.4999 | 150 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 444.0833 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 608.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 688.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1475 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2886.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 78.1666 | 67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 91.5666 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.96 | 74.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.1333 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.5332 | 137 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210.9 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280.25 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 380.55 | 177 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 164.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195.75 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 660 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1248.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 691.6 | 39 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 214.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238.732 | 213.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460.9583 | 85.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 544.595 | 73.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 638.9166 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 903.3666 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1200 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1487.2 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2206.9166 | 71 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2287.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3175 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15210 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 823.5 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1020 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1957.6065 | 300.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.5 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 536.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 823.15 | 163 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 962.1666 | 230 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1527.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3726.6666 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6825 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3294.3166 | 151 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 114.4 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 629.3333 | 59 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 789.0499 | 129 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1125.85 | 253 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1209.9998 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1244.5833 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2719.75 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194.1332 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266 | 190 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 321.25 | 257 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501.2666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 506.5332 | 131 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 637.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 690 | 60 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1075.0666 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4445 | 350 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4034.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5305.95 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7951.9999 | 192 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.02 | 45.86 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 577.7331 | 619 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 75.9833 | 47 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.8333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.4 | 182 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 431.2 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1162 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1735.5 | 89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2598.75 | 82.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3403.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.1465 | 300.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 164 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 657.6 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 795.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1102.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3222.9166 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6606 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 125 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 127.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 186.3333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 450 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 481.0999 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 573.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3134.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3526.6666 | 115 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3640 | 416 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5790 | 600 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 855 | 450 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.94996 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 462.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 500 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 750 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1813.2 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1947.3332 | 508 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2245.1419 | 438.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9581.4399 | 163.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 0.33332 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 104.4998 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.4666 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 173.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.6665 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 402.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 484.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1310.2666 | 248 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1502.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1527.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.5833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.75 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1663.9999 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4256.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 419.4666 | 121 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.4333 | 121 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4690 | 120 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.35 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.869 | 25.37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 134.8665 | 238 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 551.7479 | 363.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 552.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1448.7666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2527.8331 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.2499 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 48.9 | 163 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 152.2733 | 100.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.6666 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 179.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 431.75 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2678 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3564 | 440 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4077 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.1 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 121 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 465 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 535.3332 | 292 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1348.35 | 90.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11066.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 510 | 100 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.408 | 53.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 203.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.2666 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.9216 | 174.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 632.1 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 990.1333 | 47 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2620.1465 | 313.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4668.538 | 115.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.25 | 61 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.2 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700.4166 | 336.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 991.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1104.3 | 81.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1979.9166 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2170 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.4166 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 563.5 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1160 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1345 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3825 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.8667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.1666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 239.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 286 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 363 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 681.9999 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1398.3999 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1686.4018 | 198.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1909.5858 | 513.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2548.2 | 93 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3040 | 190 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3075.1999 | 115.32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4932.3999 | 228 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14619 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.27 | 69.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 148.2666 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155.6683 | 121.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 248.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 269.1665 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 357.525 | 204.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 841.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1012.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1293.3998 | 348 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1881 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5055.9998 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 127.8333 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 210.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 240.16 | 30.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 370 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 402 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1143.7166 | 163 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2561 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3589.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4971.19 | 105.77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 24.2667 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 2044 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2978.2497 | 495 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1140 | 30 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348.3331 | 380 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.329 | 189.82 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240.1533 | 65.2 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4950 | 40 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1869 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 311.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1748.3333 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2628.7833 | 41 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40691.2333 | 98 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.99 | 30.57 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 458.2333 | 118 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5772.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 326.6666 | 49 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6441.5 | 130 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111.9733 | 44.2 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 640 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1763.3333 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 411.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1728.9999 | 105 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220.4 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 172.5 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.25 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37265.6166 | 83 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 373.3333 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9235.6 | 88 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 888 | 40 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 778.75 | 89 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2154.7499 | 117 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5408.7 | 149 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2014 | 95 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1147.9999 | 210 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1012.5 | 150 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4123.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.04 | 111.2 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1368.1166 | 43 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 207.9 | 18 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 650-Fluidized Bed
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1907.5 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2184 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25974 | 156 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12356.6666 | 88 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37247.1333 | 82 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8190 | 27.3 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7784.1667 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 276.5 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3400.6667 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6131.405 | 35.07 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 383.6667 | 10 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39804.0333 | 83 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2277 | 46 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1082.6666 | 64 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13522.3666 | 98 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9348.3333 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 673.75 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 597 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.4 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 276.2832 | 137 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 278.5666 | 122 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 489.8833 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 633.6833 | 193 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 61.6 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 237.1833 | 107 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 366.3833 | 89 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.95 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 116.1333 | 104 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 413.3332 | 400 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3460.9831 | 739 | 1 | 1 | 0346-Pulverizer pyrite removal system | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2155.933 | 443 | 1 | 1 | 0346-Pulverizer pyrite removal system | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 768 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 470.8333 | 250 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.6667 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 194.3 | 134 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 231.6667 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 136.25 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 778.505 | 52.78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 715 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 795.9833 | 163 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 595 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.35 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 114.8 | 82 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110.05 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.9333 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 262.8 | 108 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1780.55 | 239 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 575.25 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1070.2879 | 212.64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.6667 | 10 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 401 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 542.4999 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.8 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.2 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.9 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.65 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.4 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.5 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 392.3666 | 158 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30.2166 | 37 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.6666 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.7166 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.7 | 127 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.482 | 163.32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1021.2166 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.3333 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 721.5 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.4666 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90.85 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128.8166 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 124.1333 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 61.6 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.9333 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 145.55 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.0833 | 169 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 560.4166 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.7 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.75 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.5833 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125.8833 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 253.5 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 337.55 | 157 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.6 | 24 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 104 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184.6 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.0333 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 196.4333 | 83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 650.6666 | 128 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4216 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51.9 | 173 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 151.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.4 | 64 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 123.6 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 164.45 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.1667 | 19 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 292.4 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 71.0666 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 233.7833 | 169 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 267.75 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.75 | 21 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.2 | 147 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.2666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1478.3999 | 198 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4097.1666 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.8 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 222.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.1667 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 255.6666 | 130 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1249.965 | 106.38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.816 | 10.56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.194 | 18.27 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1386 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2990 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9988.5 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 541.3333 | 112 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 476.25 | 63.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 216.3333 | 220 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.25 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.1333 | 8 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.9999 | 240 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 842.35 | 198.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 190 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2537.5 | 290 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1593.2219 | 182.43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.321 | 206.42 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.04 | 51.04 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.112 | 20.28 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.5833 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 245 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 566.6666 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2204 | 290 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.9999 | 171 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.2133 | 15.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 103.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.7331 | 356 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 263.2 | 112 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.3333 | 130 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.3333 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92.4371 | 36.73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2013.9166 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 198.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 318.6666 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 544.8333 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 392.8666 | 71 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 920.3333 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2760 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.744 | 14.16 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2744.5 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1091.8466 | 164.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.03 | 12.01 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2127.1166 | 179 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 51 | 34 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 650-Fluidized Bed
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1772.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 124.533 | 467 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1307.2 | 817 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.3331 | 290 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.9999 | 450 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 227.0495 | 717 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 283.5 | 567 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 933.8 | 667 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 490.2 | 817 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 795.5 | 215 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0358 | Oil burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 279.9999 | 150 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Winter | 764.4 | 196 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 861-CoG GT units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4485 | 460 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 14154.3667 | 38 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 73.7 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 77.4667 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 46 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 171.8166 | 169 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3761.333 | 434 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.2 | 188 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 152.5999 | 84 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 782.2499 | 315 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 568 | 568 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 7850.85 | 63 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 76 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 822 | 411 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1666 | 34 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2054.5 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12397.933 | 434 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1059.4665 | 274 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1676.9832 | 421 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.7 | 66 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1927.9332 | 478 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 75.1 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 450.8 | 184 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3936.8 | 14 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 77376.6 | 108 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 507.5 | 145 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 835.0333 | 47 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 69.6 | 24 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 172.6666 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.9165 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1524.1665 | 310 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3828.7165 | 431 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 465.3999 | 78 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2324 | 560 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3411.6664 | 460 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.7999 | 168 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18.2665 | 274 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 13441.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.5 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 438.2 | 28 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1251.1996 | 552 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 578.6665 | 434 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 57.2 | 78 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1980 | 110 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.7333 | 34 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 65.8666 | 104 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 197.2332 | 194 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 426.0666 | 83 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 488.7999 | 156 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 35074.4 | 48 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2324.75 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 480.5333 | 106 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 341.9 | 52.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 99.1167 | 19 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 24.0833 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 15.0333 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 4894.8666 | 68 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 201.3999 | 120.84 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 30.8333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1110 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 561.7998 | 318 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 20 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 21.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 97.2 | 54 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 169.442 | 37.24 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1133.2583 | 56.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 437.1 | 145.7 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 19.8613 | 37.24 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 997.6665 | 205 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 109.2373 | 37.24 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 42.4667 | 26 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 288.9 | 32.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 388.5333 | 31 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 167.96 | 51.68 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 108.5 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 303.3333 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 2.8333 | 34 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 523.34 | 41.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 877.5 | 150 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 378 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 885.9833 | 59 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 12127.3333 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 110 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5939.2666 | 143 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 33 | 11 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 4308 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8.95 | 17.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 280 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 9728.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 52.65 | 27 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 247.015 | 38.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 26.4 | 88 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4785.8665 | 274 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 3235 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 270 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6344.4332 | 143 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 206.6667 | 16 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 129.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 641.8667 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 860-Co-generator Block
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 1093.95 | 66.3 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 861-CoG GT units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 251.3333 | 58 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 470.3333 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 511.9333 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576.5594 | 82.17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 982.35 | 111 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 36.6667 | 44 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 740 | 148 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 872.3432 | 255.32 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 33.6 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 442.5 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 25 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114 | 28.5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 430 | 17.2 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 189.7999 | 156 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.5 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 659.1667 | 14 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6654.6666 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17400 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18600 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16.6667 | 4 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 62.8333 | 58 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 457.5665 | 518 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 264.6 | 28 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 321.1 | 338 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 177.5499 | 201 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185.25 | 285 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.6666 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231.4666 | 248 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.85 | 91 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 558.9 | 162 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 28324.5 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2338.52 | 32.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 203.805 | 12.94 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 26.1 | 54 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248 | 248 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 117.8666 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 605.9666 | 49 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.1667 | 25 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 34221.2 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2984.016 | 177.62 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 30.3 | 9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 119.0666 | 188 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 79456 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.1 | 33 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158 | 158 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1195.9999 | 156 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.6665 | 280 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 164.0666 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 387.8333 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3534.6 | 25.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 92.3133 | 90.8 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 637 | 98 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 89.8333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 233.3332 | 280 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 308.5333 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8297.433 | 458 | 1 | 1 | 0360-Burners | U3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1596.1663 | 610 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 650-Fluidized Bed
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 200346.5 | 337 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 138654.8 | 232 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 190 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 3431.5559 | 429.84 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 66 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 141.9 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 329 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 484.575 | 46.15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1439.3182 | 445.15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2622.8583 | 46.15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 0.49998 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 151 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2845.8 | 62 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 191.5 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 45.8666 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 269 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 26 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 492.65 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5190.8333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 93.1666 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 209 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 239 | 30 | 1 | 2 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 135.6 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 74.5333 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 263.5 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 334.5 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 719 | 30 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 12198.9833 | 61 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 645.6666 | 52 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 362.2666 | 143 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 412.38 | 26.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 95.6666 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 100.05 | 26.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 5060.65 | 26.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 91 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 55.4866 | 40.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 165.85 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2608.9 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 39.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 16.4 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 8.8 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 897.6999 | 141 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 69.75 | 93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 17.5667 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1788.85 | 7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 12030.1666 | 58 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 862-CoG steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 249.0247 | 34.91 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 270.6665 | 280 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4860.7063 | 548.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 497.7 | 237 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 637.9999 | 330 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 50.5999 | 138 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 818.4 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.9999 | 159 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 673.5175 | 357.62 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2371.4 | 142 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5549.1333 | 23 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 82.7332 | 292 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 131.0999 | 342 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4266.8232 | 548.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 171.4333 | 139 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 500 | 156.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.675 | 25.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 355.9665 | 181 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5.7 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 98.8 | 52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 143 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 183.1832 | 379 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1082.2737 | 293.83 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 66.2666 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 467.4998 | 330 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1923.7829 | 683 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 779 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.2666 | 61 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 120 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.7449 | 119.82 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 77.7 | 74 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 66.2999 | 234 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 260.3333 | 142 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.6666 | 145 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 131.4166 | 95 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 537.21 | 114.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 54.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 529.9998 | 300 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 100.2083 | 92.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 589 | 380 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 606.7708 | 156.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1213.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.9666 | 163 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424.9998 | 300 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 479.1662 | 625 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 672.9728 | 317.94 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 752.4 | 228 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 385.3667 | 22 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 559.1667 | 22 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1275.6664 | 860 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 347.75 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 97.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 21.6666 | 52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 783.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 81 | 81 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 445.3332 | 167 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 724.5833 | 23.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2536.825 | 63.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 23409.155 | 28.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Summer | 100 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 91.884 | 35.34 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4158.6 | 43.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 9382.5 | 13.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 0.072333 | 0.62 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 124.4583 | 29.87 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 8963.775 | 13.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 61.3333 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 688 | 64 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1245.1017 | 28.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 0.71467 | 0.67 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 354.7683 | 40.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1.3667 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 122.1 | 40.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 978.75 | 13.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 5985 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 13.53 | 90.2 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 109.626 | 21.78 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 357.0833 | 25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 22.8617 | 6.38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 645.25 | 43.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1923.6666 | 116 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5946.8083 | 33.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 49.5898 | 24.59 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 708 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 812.5 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1156 | 68 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 5.1667 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 200.2 | 84 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 745.65 | 13.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 792.285 | 66.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 8.22 | 164.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 49.32 | 164.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 190.9333 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 53.6667 | 23 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1493.3083 | 63.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2043.1666 | 130 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 0.68331 | 41 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 0.054166 | 0.65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 25.724 | 6.54 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 88.725 | 58.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 357 | 210 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1197.3799 | 164.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 92.8666 | 79.6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 861-CoG GT units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 13294.5266 | 79.6 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 861-CoG GT units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.9999 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.395 | 160.79 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.3325 | 11.11 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.8633 | 31.85 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165.8832 | 269 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1269.9 | 306 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80 | 16 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.8333 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 34.0416 | 81.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 160.6 | 292 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.265 | 156.53 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.8456 | 115.01 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.2216 | 161.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.7306 | 68.92 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.9526 | 126.46 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8792.7 | 742 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.7627 | 5.18 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.0008 | 63.43 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.4 | 106 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1458.5998 | 306 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177.5 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.137 | 28.26 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 120 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1204.9599 | 212.64 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2583.75 | 265 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5516 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 749.9665 | 298 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 80.4167 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 110 | 22 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 174.4166 | 65 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 184.725 | 246.3 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 132.208 | 165.26 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 58.5216 | 48.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 2899.2 | 38.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1101.75 | 195 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 21.25 | 75 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 24.66 | 164.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 104.2666 | 39.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 56.175 | 32.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 38.7499 | 75 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 16.44 | 164.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 3384.3499 | 179.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 19.2 | 2.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 9704.625 | 52.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 24.8516 | 48.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.1666 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.2 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.8333 | 130 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.9499 | 117 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 357.8666 | 122 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.4666 | 64 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 157.5666 | 65.2 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 307.08 | 85.3 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35 | 60 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2437.3331 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5532 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2629.75 | 157 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44 | 80 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 284.1666 | 110 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222 | 111 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1337.0499 | 363 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.9999 | 120 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 114.5833 | 125 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2798.5832 | 355 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314.4166 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 937.5 | 75 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1054.1666 | 275 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455.8663 | 526 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1020.4165 | 395 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4378.0832 | 535 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1192.3565 | 522.2 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 40.3664 | 346 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112 | 64 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196.95 | 39 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 992 | 160 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.9999 | 420 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 327.6998 | 339 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153 | 45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 448.3375 | 137.95 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 47.9166 | 125 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.75 | 215 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.65 | 231 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 981.6665 | 380 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Off-Peak | 30957.7915 | 642.5 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.0666 | 121 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 287.5 | 75 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.6665 | 220 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2413 | 635 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 44.7333 | 44 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1475.0166 | 269 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 36.1667 | 7 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 63.308 | 37.24 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 2413.8666 | 64 | 1 | 1 | 0385-Igniters | U2-Forced - Delayed | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 1.8333 | 55 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 7.3333 | 55 | 1 | 2 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 2636.25 | 22.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 545.05 | 11 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 758.333 | 500 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 144 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 410.6665 | 280 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 779.1 | 106 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 533.333 | 500 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 408.333 | 500 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 374.5332 | 212 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6735.6664 | 334 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33587.4663 | 478 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6718.7831 | 673 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 43608.4 | 51 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 539.7332 | 253 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 407.55 | 143 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 109 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25.75 | 103 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 102.4666 | 58 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 568.6499 | 153 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1812 | 151 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 136.4666 | 89 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 21968.2499 | 153 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.5833 | 85 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11438.9999 | 108 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 87840 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 386.1 | 143 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 133.248 | 41.64 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 800-Miscellaneous
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 432.5 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 189.5833 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 193.5 | 387 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 127.9999 | 384 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Winter | 209.9999 | 180 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 990 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 89.3333 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 278.0597 | 22.01 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 89.498 | 36.78 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 30489.875 | 6.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 154.0933 | 17.78 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1313.27 | 21.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 144.0833 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 567.6 | 3.3 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 67.5 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 176.1633 | 64.45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 319.8 | 123 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 283.5 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 710.6167 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 71.4163 | 17.78 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 56.5 | 45.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15.4 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 36.6666 | 50 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.5117 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 17.5 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 451.8405 | 38.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9.1666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.9353 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278.6667 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.295 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1030 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2919.5833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 391.6092 | 25.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1244.895 | 50.13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 10.3333 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1498 | 107 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1054.85 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1751.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13122.9166 | 62.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.554 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107.7333 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1490.05 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39 | 52 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.9857 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.777 | 5.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 30.9333 | 32 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 724.35 | 439 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5975 | 50 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 27.3 | 42 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 65.7 | 73 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 401.5 | 73 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2896.6666 | 40 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 464.9666 | 37 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 164.5 | 35 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 82.5 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 54.6 | 36 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1000 | 50 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 210.5 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5.0667 | 38 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.75 | 25 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 19.1667 | 50 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53.9999 | 81 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56 | 40 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 225.3333 | 80 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 185 | 18.5 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1293.3333 | 80 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7995.8333 | 50 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2669.333 | 455 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 807.16 | 23.74 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2244.6665 | 455 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9217.9999 | 330 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1630.4165 | 455 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.8333 | 76.1 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.8 | 48 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.8 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.75 | 95 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 129.6 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 96 | 96 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.6 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 42 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.2 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.1 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.5 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.5 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.8 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.1 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.75 | 159 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.3 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.8 | 76 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.3333 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.75 | 31 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.3333 | 31 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.0833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.7666 | 31 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.2666 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 791.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 359.2 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.4 | 102 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.6666 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.5 | 70 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3333 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.7833 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.5 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8333 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.7 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.5333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6851.7833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.9 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.4 | 48 | 1 | 12 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.9999 | 90 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.3333 | 80 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.8166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159 | 159 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 447.9167 | 25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9505.15 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.85 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.4 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.9166 | 31 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.4 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.1166 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.25 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.9166 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.2666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 90 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 411 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 496.9166 | 67 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.0333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.9166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.9 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.8333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3 | 26 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.1 | 31 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.15 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.6166 | 31 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.2 | 31 | 2 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.5 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.1 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99 | 49.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.6666 | 145 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 432 | 576 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.4 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8333 | 95 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.2 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.4167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2986.9 | 25.1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.5833 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 80 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.5666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 40 | 2 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 280 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 278.85 | 117 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.3333 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 90 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8333 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6 | 66 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.05 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1238.7999 | 114 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6 | 26 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.55 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6333 | 26 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.4 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 659.8666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.1833 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.65 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.8333 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.55 | 31 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1667 | 26 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.6375 | 11.13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 30 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.4666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.5 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.6333 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.6666 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 27.9166 | 67 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3461.3332 | 295 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 1169.355 | 37.3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1863 | 405 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1218.9999 | 345 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2441.25 | 315 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 104015.4998 | 285 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 98122.5 | 525 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1741.1333 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1834.2333 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 57.1666 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1376.2333 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 10.6166 | 63.7 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 291.25 | 75 | 1 | 1 | 0440-Fuel oil pumps (general) | U2-Forced - Delayed | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3448.4997 | 495 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 141.6999 | 78 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 553.6597 | 437.1 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 106.5999 | 78 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 837.2 | 78 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 998.1665 | 530 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1129.9998 | 600 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.8333 | 10 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.3333 | 10 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35 | 15 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.75 | 15 | 1 | 1 | 0460-Fuel oil atomizers | D2-Forced - Delayed | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63 | 90 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 830.4998 | 330 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 396 | 330 | 1 | 1 | 0470-Oil and gas fires | SF-Startup Failure | 100-Fossil-Steam
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 484.5083 | 26.5 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 467.2833 | 26.5 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 18.9833 | 17 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 38.9332 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 86001.8666 | 122 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 98887.3998 | 318 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 702.4833 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 418 | 380 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10.6333 | 2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 7 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1583.5999 | 222 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59260.9332 | 179 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 700.8 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1222.4331 | 338 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 42 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 77.8665 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1342.68 | 335.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60386.6664 | 800 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 60 | 120 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 12140.3329 | 602 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 444.8932 | 333.67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 946.95 | 321 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3778.2 | 54 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 321.445 | 12.13 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 610.1332 | 352 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2366.733 | 524 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 43.9999 | 330 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 91 | 260 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 703.3332 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1017 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 462.9166 | 101 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 12.6332 | 379 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 22.7998 | 342 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 74.6666 | 320 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 113 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 897 | 5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5.25 | 35 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 35.6 | 24 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 183.1832 | 379 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59049.1166 | 179 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 61.75 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 67703.0666 | 136 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1151.3328 | 785 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6890.5997 | 789 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Oil | OL | 800 | Miscellaneous | MRO | Off-Peak | 31.878 | 9.24 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 600.65 | 293 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 484.9998 | 291 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1144.5999 | 291 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 330 | 200 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 9.75 | 9 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 41.6667 | 20 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 41.8667 | 16 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 14.0833 | 13 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 52.3333 | 20 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 42.25 | 39 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 208.3333 | 100 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 48.7333 | 68 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 104.6666 | 40 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 345 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76720.25 | 773 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4471.9 | 197 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14100 | 600 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 70.2945 | 34.29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 593.8333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 645 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1677 | 156 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 486.8333 | 115 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 240.3333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2405.8665 | 416 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 569.9398 | 289.8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 398.3333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 504.1667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7766.2662 | 742 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 22.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 2396.279 | 46.29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 55167.0949 | 246.3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 77387.4 | 162 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 380 | 190 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 249215.1 | 129 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 836 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 935.8146 | 162.28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 823.65 | 164.73 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 507 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3517.3333 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.4166 | 49 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1881.3332 | 170 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 16472.4833 | 29 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 357.8333 | 113 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 153.8333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35318.8 | 184 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 79.5167 | 13 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 390 | 90 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 130.5 | 174 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 906.2497 | 375 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18.3333 | 44 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1183.6 | 33 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 998.2 | 124 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2189.9333 | 214 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 210 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 5.7 | 38 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1804.2667 | 17 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2687.3 | 42 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4742.8333 | 199 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 436.0333 | 127 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 7252.6666 | 230 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 4266.5 | 230 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 7045.55 | 124.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18785.25 | 115 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 93537.7332 | 412 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28709.5332 | 412 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6.6666 | 50 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29295 | 630 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2388.6331 | 353 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8598.065 | 124.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9395.4995 | 690 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13717.5833 | 115 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 116.8 | 12 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.5 | 30 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9705.9995 | 690 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2493.15 | 99 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 6295.2716 | 124.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 308 | 154 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3272.8332 | 538 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.75 | 25 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13088.2382 | 324.1 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3589.4331 | 419 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26467.3164 | 361 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134333.3328 | 800 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 37370.1497 | 417 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21343.5 | 465 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.6666 | 40 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 527.25 | 37 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 90 | 12 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3 | 30 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11160.65 | 124.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105978 | 680 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 122.2 | 39 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 542.4998 | 525 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 802.75 | 247 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 297.5 | 350 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 6374.4999 | 165 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 5945.1998 | 267 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1048.2333 | 82 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 400.5 | 267 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 550.3666 | 79 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1427.5832 | 185 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 14083.6666 | 230 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 470.4 | 72 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 643.2 | 192 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 239.1999 | 156 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Winter | 644.9999 | 180 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 197.5999 | 156 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 5874.4166 | 157 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1043 | 14 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 7524 | 120 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 4675.9999 | 210 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 315 | 210 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 140.6667 | 20 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 709.5 | 165 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 2049.2666 | 236 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 653.3333 | 100 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 46.2 | 21 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 861-CoG GT units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 780.9999 | 426 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14755 | 1300 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.3833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.95 | 3.65 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7122.5 | 770 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 547.08 | 5.64 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8698.9499 | 351 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8104.7483 | 120.1 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 1011 | 20 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.4 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 1.8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6 | 24 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61 | 6.1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.2 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 474.81 | 3.99 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.45 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3902.85 | 177 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15275 | 1300 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 6888.5582 | 456.7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 39.4833 | 23 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 194.4 | 54 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 6569.5665 | 506 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 3936.5841 | 277.55 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 525.3 | 51 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 243.7499 | 225 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 254.0999 | 126 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 352.4998 | 225 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Off-Peak | 20058.6666 | 160 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1466.8 | 193 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 127.8566 | 63.4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 192 | 320 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 320 | 320 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 77.3333 | 160 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 90.6666 | 160 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 246.54 | 82.18 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125848.6268 | 814.73 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.3759 | 98.79 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107637.2901 | 813.79 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6922.1995 | 747 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 10962 | 522 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 40154.2665 | 244 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 21171.2614 | 334.9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 9198.1332 | 272 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 29854.6231 | 383.9 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 31224.3 | 222 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 12433.2 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 4581.5 | 154 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 5630.025 | 138.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 510.9433 | 90.7 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1764 | 180 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 7890.9999 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 714.6026 | 261.44 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1565.5482 | 270.7 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 20142.1999 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 386.466 | 141.39 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1176 | 105 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4040.61 | 99.4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 1869.4765 | 321.4 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44579.9999 | 225 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5104.6666 | 104 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 428.6356 | 262.43 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 438.1999 | 84 | 2 | 2 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 274.512 | 261.44 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 2382.9 | 169 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 148.4595 | 141.39 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1551 | 110 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 48.3 | 322 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1370.6666 | 320 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 308.7015 | 141.39 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1121.5832 | 215 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 247.5 | 225 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 743.9833 | 49 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18469.7099 | 359.1 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.35 | 11 | 1 | 1 | 0550-Reheat steam relief/safety valves | D3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8100.3333 | 190 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 248.6664 | 746 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 594.595 | 109.1 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8479.5328 | 746 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3635 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 135.5333 | 214 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 285.1666 | 290 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 154.6667 | 20 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 130.1165 | 211 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 571.2832 | 227 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 2918.9 | 202 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 5706.5 | 202 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 453.65 | 211 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 3590.7499 | 159 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 4051.3666 | 179 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 4913.55 | 179 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 23984.75 | 197 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 4359.2499 | 159 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 133.95 | 141 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 4407.25 | 305 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 334.8832 | 283 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 11803.5 | 152.5 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Summer | 16564.9998 | 300 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Winter | 224.933 | 482 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 9155.0831 | 305 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 531.1466 | 173.2 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 958.65 | 99 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 36.9 | 82 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 61.8333 | 70 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 166.8333 | 70 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36.1666 | 70 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234491.9999 | 180 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 27951 | 363 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 88549.2 | 972 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U3-Forced - Postponed | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 17759.2663 | 547 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2115.3329 | 668 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 13.9999 | 120 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 173.6498 | 226.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1193.9092 | 261.44 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 4122.3 | 182 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1304.7466 | 140.8 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1882.0133 | 156.4 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2144.85 | 181 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 16747.0332 | 182 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 12 | 120 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 36583.7332 | 173 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 77.9166 | 275 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1942.7333 | 181 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 61.2332 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 78.9332 | 128 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 645.5896 | 141.37 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 932.2266 | 100.6 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4553.3333 | 100 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 870.1166 | 83 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 746.4265 | 243.4 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 42.5332 | 319 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 37.0333 | 101 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2672.7 | 118 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 18645.9666 | 118 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 2962.5 | 250 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 18609.0666 | 88 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Winter | 832.2999 | 174 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 861-CoG GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 440.0666 | 92 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 862-CoG steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1654.0331 | 347 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 14800.5998 | 258 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 63.525 | 181.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 181.3333 | 136 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 932.7916 | 152.5 | 2 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 321.1 | 169 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 141.2 | 105.9 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 16017 | 281 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3076 | 120 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1834.9998 | 300 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 24.5 | 21 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 155.3998 | 252 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3424 | 120 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1203.3333 | 38 | 1 | 1 | 0570-Other reheat steam problems | D3-Forced - Postponed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1737.5 | 25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 822.0833 | 25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 74874.1328 | 824 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 871.68 | 4.54 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 12963 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 21148 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11 | 22 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 10799 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1848.35 | 21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 9400 | 25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4943.25 | 507 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 17.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 567 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 747.5 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 316983.9998 | 480 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 198000 | 550 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 437.6165 | 217 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1803.7498 | 225 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 348 | 174 | 1 | 1 | 0570-Other reheat steam problems | SF-Startup Failure | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 491.7 | 298 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 300.4832 | 149 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 195.833 | 470 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 514.5999 | 372 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 66.1466 | 90.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1413.6 | 372 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 165.85 | 93 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 978.0333 | 122 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 221.6665 | 190 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1650.5166 | 167 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1965.0332 | 167 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 5868.4666 | 164 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30627.6699 | 301.8 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6432.9 | 523 | 1 | 1 | 0580-Desuperheater/attemperator piping | U2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10317.6666 | 130 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1171.2 | 384 | 1 | 1 | 0580-Desuperheater/attemperator piping | D2-Forced - Delayed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1676.5666 | 106 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10103.4998 | 330 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4512.7831 | 329 | 1 | 1 | 0580-Desuperheater/attemperator piping | D3-Forced - Postponed | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3971.7097 | 390.66 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.8333 | 130 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 252.1667 | 17 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 800-Miscellaneous
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 733.72 | 21.58 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1093.4666 | 236 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3663.0165 | 271 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1858.7333 | 196 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 329.6333 | 31 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 589.4999 | 135 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6968.4331 | 338 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 80 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19.2 | 48 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 860 | 215 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6187 | 230 | 1 | 1 | 0590-Desuperheater/attemperator valves | SF-Startup Failure | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43038.3331 | 850 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 272.25 | 165 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 312.6665 | 280 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 306.6666 | 115 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 912.9332 | 328 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1203.75 | 321 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 466.6666 | 160 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19258.4499 | 417 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 10330.5 | 485 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1484.95 | 51 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5085.5415 | 206.31 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5730.9832 | 179 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165 | 55 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 723.8832 | 257 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1413.3333 | 160 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 132 | 80 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 186.1667 | 10 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173 | 34.6 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1218 | 609 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 33375.7425 | 382.53 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19294.6663 | 580 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 860.7665 | 217 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180 | 180 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2180.4 | 69 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3999.5 | 421 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 280.5832 | 481 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12611.1329 | 638 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 759.3331 | 335 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | SERC | Summer | 264.225 | 19.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 800-Miscellaneous
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1513.4165 | 635 | 1 | 1 | 0610-Desuperheater/attemperator drums | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 44783.333 | 500 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2199.6 | 564 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 50.4895 | 2.41 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.7 | 3.5 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2788 | 340 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 46.9 | 134 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 149.981 | 4.98 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4287.4999 | 147 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106823.2662 | 742 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11571.9998 | 330 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8693.7662 | 742 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3917.6665 | 644 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7682.1331 | 832 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29466.6661 | 832 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2793.9998 | 660 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10613.3992 | 1197 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33097.2828 | 773 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 911.0331 | 302 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 461.933 | 533 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5290.6665 | 620 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11745 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.1996 | 576 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 380.2666 | 248 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24991.1662 | 691 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12300.4 | 644 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 391.7333 | 208 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11060.7331 | 661 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60600 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 316.1 | 218 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26975.3164 | 469 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12817.1665 | 530 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1326.8331 | 419 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128541.25 | 1315 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36616.1664 | 746 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3369.2999 | 198 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13997.75 | 365 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10642.5 | 330 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1191.6666 | 260 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1313 | 260 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U2-Forced - Delayed | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 2661.75 | 63 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 9914.5 | 251 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 871.5 | 83 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 860-Co-generator Block
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5197.2165 | 199 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2137.5 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17372.25 | 15 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 364.1667 | 25 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12417.3331 | 670 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39311.4329 | 638 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252.4667 | 14 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 462.3331 | 365 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200.06 | 14.29 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13156 | 220 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3684.6667 | 8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6365 | 670 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 11785.6 | 508 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2020 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 276 | 460 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 26857.9666 | 242 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1581 | 310 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 16175.25 | 395 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8581.95 | 489 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2004.725 | 44.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 177.0082 | 193.1 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 262.4998 | 225 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1066.4166 | 335 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 450 | 75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 585.65 | 13 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 850 | 75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 186.6666 | 160 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 636.6666 | 200 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Winter | 6210.2666 | 94 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 861-CoG GT units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 3501.5333 | 53 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 862-CoG steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 7.5 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57723.8999 | 234 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2158.45 | 881 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 222.8233 | 64.9 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 621.6 | 103.6 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 850-Combined Cycle Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 309.4665 | 211 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 785.1998 | 312 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 684.6 | 126 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 50.4 | 126 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 31.5 | 126 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 150.3 | 167 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 83.8499 | 193.5 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 297.5 | 175 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 344.4733 | 63.4 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 15.85 | 63.4 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 38.4999 | 105 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 25.36 | 63.4 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 712.88 | 127.3 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175.9333 | 116 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 16942.8665 | 321.7 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 650-Fluidized Bed
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 8567.4 | 327 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 4662 | 252 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 1227.177 | 64.93 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 1289.9426 | 64.93 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 1431.9833 | 151 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1847.55 | 98.1 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0720 | Blowdown system controls / instrumentation | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 291.4549 | 246.3 | 1 | 1 | 0720-Blowdown system controls / instrumentation | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1625.3328 | 848 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1070.2166 | 157 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 851-CC GT units
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 977.5 | 138 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.2 | 112 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1160.4999 | 165 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 480 | 120 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 28893.6666 | 98 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3654.3999 | 192 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 16896 | 440 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 169 | 338 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4654.9998 | 300 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116662 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 45403.3333 | 100 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4752.333 | 530 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54229.9998 | 600 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2596.5328 | 728 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1943.333 | 440 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93860 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14784 | 352 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6847.0333 | 17 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 300 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 503.2497 | 495 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1616.4166 | 163 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5102.0833 | 79 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1710 | 600 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 263.0896 | 72.41 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 358.1332 | 316 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89201.8333 | 95 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19383.4664 | 352 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9026.6666 | 40 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18595.85 | 67 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.7666 | 209 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 893.7999 | 246 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19592 | 40 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1269.5831 | 275 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 36792 | 219 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4239.9999 | 300 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25696.1665 | 530 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16799.4167 | 35 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12419.5 | 30 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240595.9 | 92.1 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15433 | 220 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 94.25 | 145 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 852-CC steam units
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27086.6666 | 80 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1139.5 | 530 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1519.333 | 530 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 626.9997 | 495 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27552.9331 | 742 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U2-Forced - Delayed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 462902 | 106 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2648.3 | 746 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 662.4 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3824.3328 | 770 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 533.5996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2202.48 | 314.64 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11941.5998 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1887.84 | 314.64 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7840 | 800 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 855.6 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1002.7996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7609.2 | 746 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14833.4665 | 184 | 1 | 1 | 0760-Boiler recirculation valves | U3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8966.6 | 419 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5579.6664 | 881 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 784.3 | 71.3 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 1042.2 | 115.8 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 660.1667 | 17 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 176.4582 | 192.5 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 851-CC GT units
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 209.9165 | 229 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1175.25 | 15 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 120 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2490 | 15 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228968.3331 | 790 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8369.6664 | 340 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1212.165 | 24.3 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 650-Fluidized Bed
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 8948.9731 | 401.9 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 753.35 | 247 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 224.25 | 299 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1745.15 | 57 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 3973.75 | 275 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 9433.78 | 56.83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 4465.95 | 57 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 9367.5166 | 161 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 10206 | 162 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6300 | 100 | 1 | 1 | 0775-Economizer piping | D2-Forced - Delayed | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 1836 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 4590 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 1785 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 2499 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 3544.5 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 684.75 | 83 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 5814 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 1785 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 1627.6533 | 26.8 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 862-CoG steam units
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44427.7 | 698 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 19796.1 | 85.5 | 1 | 1 | 0780-Headers between tube bundles | D1-Forced - Immediate | 850-Combined Cycle Block
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 42583.5999 | 174 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 850-Combined Cycle Block
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 28713 | 255 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 850-Combined Cycle Block
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 2465.775 | 175.5 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 850-Combined Cycle Block
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 10586.4 | 176 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 851-CC GT units
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8572.0999 | 138 | 1 | 1 | 0780-Headers between tube bundles | D1-Forced - Immediate | 852-CC steam units
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 448.4333 | 22 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 460.1667 | 22 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 397.9166 | 191 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11884.9998 | 300 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 336091.65 | 373 | 1 | 1 | 0782-Headers and caps | U2-Forced - Delayed | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 578.6 | 22 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 685.9 | 57 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D3-Forced - Postponed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 9180 | 108 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 17199.828 | 333.33 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 14688.7418 | 333.33 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2016 | 240 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1402.6666 | 80 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1182.36 | 47.2 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4637.97 | 177.7 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3621.3332 | 280 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 15039.9999 | 300 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1737.3999 | 204 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 371.4316 | 102.7 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Summer | 31297.636 | 98.04 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 2564.1 | 126 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 8257.5999 | 156 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 22.275 | 49.5 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 50.4 | 126 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1754.9666 | 163 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 6897 | 76 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 6870.7165 | 247 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 4050.6666 | 70 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1101.6 | 102 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 71.5 | 13 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 25.36 | 63.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1290.19 | 63.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93746 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.4166 | 275 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 536.406 | 206.31 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 816 | 48 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 371.875 | 17.85 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3581.4998 | 285 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16522.9166 | 275 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 682 | 440 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 160.6 | 292 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 629.933 | 859 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 877.5 | 270 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1962.4997 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18893.6 | 836 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81514.4333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.5 | 13 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 334.05 | 393 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.3332 | 280 | 1 | 2 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 912 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1843 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 131.3999 | 108 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 358.1999 | 108 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 182.4 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 883.6944 | 206.31 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1241.9997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 288.8 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2826 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2451 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 182.0832 | 475 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189.1174 | 206.31 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4636.5 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28272 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330.7497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6380 | 275 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1134.9333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 777.6 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 7610.9281 | 624.7 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 5690.6333 | 79 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 800-Miscellaneous
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1364.0666 | 25.9 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1580 | 30 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 631.75 | 35 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 498.3 | 151 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Winter | 200.9999 | 180 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 543.6 | 151 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 65.4333 | 151 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 835.5333 | 151 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 211.4 | 151 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 11368.2333 | 83 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 860-Co-generator Block
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 4183.2 | 83 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 62.725 | 19.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 13111.4666 | 112 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 93.5 | 110 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 527.0333 | 163 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 5626.1331 | 308 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 9.0883 | 28.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 226.2165 | 277 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 22.5 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1324.6665 | 397.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3478.1998 | 558 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 586.1333 | 112 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 340 | 85 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 121.56 | 202.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 45.8666 | 86 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 355.6933 | 103.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1491.4666 | 112 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 172.5 | 230 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 225.89 | 322.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 9866.18 | 293.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 118.1833 | 202.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 558.5999 | 342 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 244.3332 | 293.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4226.1333 | 112 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2142.5666 | 323 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 140.6665 | 422 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 16548 | 112 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 4949.0665 | 268 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 268.2 | 298 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 778.4 | 278 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 129.2 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3336.6 | 249 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 8.5 | 17 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 33.5 | 30 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 11563.2 | 264 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9.35 | 187 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 113.75 | 162.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 134.5666 | 183.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 120 | 150 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 15436.9832 | 307 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Winter | 73478.9999 | 180 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 14.725 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 202.2833 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 250.6833 | 169 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1150.05 | 187 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 155.1666 | 37.24 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 215.05 | 187 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 819.3833 | 211 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 35.7333 | 67 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 81.6 | 204 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 2637.6665 | 193 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 236.35 | 163 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2389.9833 | 193 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 63.65 | 67 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 88.8566 | 140.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 240.2999 | 162 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 75.5 | 151 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 40.3 | 93 | 2 | 2 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 11.45 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 21.7 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 37.2 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 196.25 | 157 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 204.552 | 227.28 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 259.5333 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 716.3332 | 307 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 8009.8332 | 170 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 16.275 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 232.8165 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 573.3333 | 160 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 436.7998 | 234 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 8492.6958 | 227.28 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 41.075 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 13.95 | 93 | 2 | 2 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2358.4125 | 137.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 99.0733 | 135.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 163.85 | 113 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 5902.0649 | 157.95 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 11.9 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 75.9999 | 228 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1460.5 | 254 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 74.9166 | 145 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 132.7208 | 150.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 470.85 | 129 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 345.6665 | 244 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 1448.85 | 117 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8.075 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 488.3125 | 150.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2422.85 | 141 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 102.36 | 255.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 147.0666 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 187.5 | 150 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 522.072 | 217.53 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 49.5 | 99 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 381.0332 | 322 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 47.85 | 319 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 138.2332 | 319 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Summer | 8091.8749 | 160.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 50.75 | 145 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 18.2666 | 109.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 30.1708 | 72.41 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 1598.9999 | 117 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 266.5 | 10 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 438.6999 | 160.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 63.3333 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 608.4 | 234 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 91.3333 | 109.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 120.8333 | 145 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 247 | 190 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 267.9458 | 150.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 31.535 | 111.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | SERC | Off-Peak | 2058.75 | 75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | SERC | Summer | 1700 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Winter | 80.7332 | 173 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 100 | 50 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 45.9293 | 98.42 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 378.4166 | 239 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7.8999 | 237 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 174.7998 | 228 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 17.2833 | 207.4 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3992.8 | 248 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 26.9999 | 162 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 239.1331 | 422 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Winter | 272 | 272 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 239 | 239 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 691.5999 | 228 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 186.1998 | 228 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 769.1665 | 325 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 720.4166 | 175 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 710.4999 | 174 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 614.4833 | 229 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2425.3 | 307 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 251.2499 | 225 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 65.6166 | 127 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 266.2499 | 225 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 202.2833 | 229 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 284.9998 | 225 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1248.9 | 181 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 277.0833 | 175 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 73.6 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1001.25 | 225 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 21.3332 | 128 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 959.0632 | 193.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 461.335 | 188.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 1255.5 | 162 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 21.1666 | 127 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 194.65 | 229 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 34.9283 | 110.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 570.1572 | 251.54 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1056.7581 | 300.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 358.4 | 256 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 831.9 | 177 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 309.639 | 281.49 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 712 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 271.9998 | 255 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 114.8549 | 181.35 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 8.4999 | 255 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1530.0999 | 160.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 291.2275 | 301.27 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 34.7066 | 109.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 257.9291 | 150.25 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 178.6666 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 803.9665 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 131.782 | 188.26 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 42.6666 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 132.7208 | 150.25 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 873.29 | 140.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 97.5 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 38.36 | 109.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 29.05 | 21 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 426.6666 | 64 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 77 | 92.4 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 2179.1 | 92.4 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 37.8 | 126 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 17.7333 | 38 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3368.6666 | 163 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 369.5835 | 223.99 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 530.3332 | 215 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 18.415 | 38.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 64.135 | 38.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2056.7 | 157 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 118.0666 | 161 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 124.1999 | 162 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 152.1333 | 163 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 618.75 | 165 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 649.8165 | 307 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 384.3999 | 186 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 799.0999 | 183 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 42.9332 | 322 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2124.9999 | 150 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 127.5666 | 89 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 462.7749 | 160.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 913.5 | 315 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3815.2333 | 166 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 262 | 60 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 19.02 | 63.4 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7030.4 | 169 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 53696.9333 | 169 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 203301.3666 | 169 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 596169.1996 | 552 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63410 | 340 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 861.0997 | 474 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240047.4566 | 248.9 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 5784 | 241 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 24836.3666 | 191 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 391959.3 | 509.7 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37456.4036 | 175.18 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12285 | 390 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7978.1 | 361 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 105.5833 | 35 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 70337.4998 | 750 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 32180.4166 | 169 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 279072 | 38 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4320 | 450 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1755 | 390 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7929.6 | 336 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 81511.9996 | 552 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13224 | 19 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14136 | 19 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 490.5833 | 35 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 56388.12 | 229.22 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 850-Combined Cycle Block
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 108.6995 | 167.23 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13113.6191 | 167.23 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 12066.25 | 147 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 21077.3333 | 247 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11252.85 | 63 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8828.6665 | 380 | 1 | 1 | 0830-Doors | SF-Startup Failure | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15642 | 330 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120846 | 1320 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1915.8 | 412 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14309 | 820 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2346.6664 | 800 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16567.95 | 63 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19944.1665 | 325 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7270.6661 | 820 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1779.5665 | 271 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 465 | 20 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12624.3329 | 626 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10004 | 244 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10564.3331 | 820 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 3512.6816 | 151.3 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23064.0999 | 183 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 345.6 | 28.8 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 800-Miscellaneous
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1403.78 | 103.6 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 9494.125 | 251.5 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1318.6666 | 230 | 1 | 1 | 0830-Doors | SF-Startup Failure | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 16984.8 | 126 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1637.5499 | 81 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 1533 | 73 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 8546.32 | 63.4 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 882 | 42 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 909.75 | 45 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 762 | 120 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | WECC | Summer | 556.2167 | 23 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | WECC | Winter | 5743.65 | 177 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 3472.15 | 107 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 166110.4164 | 355 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 31270.3664 | 397 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 467.4999 | 255 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 83208 | 80 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 1045 | 19 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 800-Miscellaneous
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 2972.5 | 20.5 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 800-Miscellaneous
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 3713.35 | 69 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 10015.8333 | 85 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1310.9999 | 90 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 8449.9666 | 106 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 850-Combined Cycle Block
0848 | Inlet panel | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 445.2 | 126 | 1 | 1 | 0848-Inlet panel | U1-Forced - Immediate | 851-CC GT units
0848 | Inlet panel | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 149.85 | 37 | 1 | 1 | 0848-Inlet panel | D1-Forced - Immediate | 852-CC steam units
0848 | Inlet panel | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 224.0133 | 63.4 | 1 | 1 | 0848-Inlet panel | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 357.5 | 14.3 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 644.0333 | 139 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 18174.25 | 139 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 56076.0132 | 416.2 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 234.3 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 914.0333 | 17 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64495.3331 | 712 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362.5 | 30 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 312.9 | 18 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 822.4996 | 525 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1937 | 26 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 800-Miscellaneous
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 34689.82 | 98.04 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 850-Combined Cycle Block
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 1163.4 | 126 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Oil | DI | 851 | CC GT units | SERC | Winter | 87.15 | 83 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 585.3933 | 63.4 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7958.8333 | 34 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28800 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 335.92 | 176.8 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5121 | 10 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 462.8557 | 32.18 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7310.5667 | 38 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 298.9997 | 390 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14703.4333 | 26 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.4 | 138 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83022 | 606 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 8218.0194 | 382.53 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 535.5 | 119 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 839.04 | 136.8 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 46.6666 | 175 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1768.4333 | 77 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17400 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31949 | 43 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2770.8999 | 363 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2838.3333 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 797.3333 | 160 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17361.4997 | 390 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28892.4999 | 390 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1312.5 | 62.5 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 850-Combined Cycle Block
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 7578.8999 | 162 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 851-CC GT units
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 8467.7833 | 181 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 852-CC steam units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 26.4 | 88 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1118.41 | 115.3 | 1 | 1 | 0857-IP Drum relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7708.35 | 201 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5895.9999 | 201 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7889.25 | 201 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8780.1999 | 156 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63 | 42 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.6666 | 95 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.9167 | 47 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.65 | 97 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.1 | 118 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.05 | 97 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.75 | 85 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 458.5 | 131 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.0167 | 6.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 453.3332 | 400 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2014.8 | 219 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4.8333 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3057.015 | 237.9 | 1 | 1 | 0870-Soot blowers - steam | U1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1144.15 | 147 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 702.8666 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4987.5 | 75 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 22278.5333 | 52 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 128.3333 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 4.433 | 4.29 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 521.85 | 147 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 17670.2499 | 195 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 62.9333 | 32 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1.6533 | 3.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | SF | Startup Failure | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2134.1667 | 50 | 1 | 1 | 0870-Soot blowers - steam | SF-Startup Failure | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 835 | 100 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1005.1 | 138 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4374.9999 | 150 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296 | 37 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 125.8833 | 91 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 20.826 | 8.01 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 64.5833 | 31 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3024.2666 | 176 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1283.7499 | 75 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.5 | 190 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2779 | 35 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.25 | 7 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392.6665 | 620 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 414.6666 | 40 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.53 | 25.1 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 591.9999 | 96 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 333.4999 | 138 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25091.58 | 69.57 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.05 | 37.8 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.75 | 55 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47.25 | 45 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.486 | 41.66 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.5 | 30 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 313.333 | 470 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 451.6666 | 100 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 375.6665 | 196 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 118 | 118 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1280 | 200 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204 | 85 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2932.1666 | 146 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 123 | 6 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.3331 | 380 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275.6167 | 11.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7137.1665 | 187 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 762.5066 | 157.76 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2320.188 | 100.08 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 572.45 | 10.7 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 117.8333 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3925.7165 | 539 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 434.1667 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6961.5999 | 182.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8302.7999 | 198 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 765.666 | 154.68 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6246.803 | 126.71 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.0833 | 25 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 945.395 | 171.89 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1202.7999 | 186 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 804 | 134 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 744 | 186 | 1 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 38692.1333 | 184 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U3-Forced - Postponed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1847.4749 | 186.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9.47 | 9.47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 29.75 | 17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 32.0167 | 17 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 131.4833 | 49 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 588.7999 | 192 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12149.6665 | 317.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1384.758 | 161.96 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4302.36 | 150.96 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1459.2666 | 118 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1200 | 200 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 88.2 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | SERC | Summer | 637.975 | 19.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 379.5 | 25.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3930.4333 | 122 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10760.1666 | 230 | 1 | 1 | 0885-Fly ash Removal System - wet transport | U2-Forced - Delayed | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1177.0617 | 20.3 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126 | 280 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3393.25 | 277 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.2667 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1122.6 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2176.25 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 46.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31555.6662 | 691 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7558.8329 | 665 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.7666 | 46 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.5 | 17.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 42.3666 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 70.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.7667 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2382.05 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1602.3332 | 460 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 492.8 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 46 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3105.75 | 505 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1025.15 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1832 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2497.8 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.75 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 172.2 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 643.3 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1011.25 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2978.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67617 | 495 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 669.5 | 130 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1298.4999 | 210 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 105.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1652.8166 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 28.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195.0667 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 689.6 | 16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.45 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 115.5 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 192 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1085.75 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1738 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 28.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740 | 37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95619.3329 | 680 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 389.25 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1512.75 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35925.1664 | 415 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8362.0832 | 427 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 867.9375 | 46.29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1858.2666 | 308 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 217.2333 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3087.5 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 111.8 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156.8667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 334.1333 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 391.3833 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 803.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 925.1667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39874.9999 | 330 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 57.9 | 6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 106 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 319.8 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 815.3167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 123.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.15 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 139.8 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 367.7667 | 17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 655.4667 | 16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 771.3333 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1003.75 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 85.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10030 | 200 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 45.6 | 38 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 90 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1949.3333 | 160 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 30 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 80.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 599.6667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 456.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 776.3167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.8 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.8 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126.8667 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 219.8167 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 333.1333 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 398.0667 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 449.9833 | 29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17178.4998 | 510 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2568.7499 | 225 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1652.6389 | 336.13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 205.7 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 5.75 | 1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 33.5667 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 89.8333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.25 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1819.5833 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 62.65 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.1667 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 836.1 | 18 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1039.5 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1106.95 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 38.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 46.3333 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 65 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 611.028 | 46.29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2878.4166 | 32.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 78.4 | 9.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 110.2167 | 17 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 975.8 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 20.4 | 6.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 35.0533 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 722.4 | 25.8 | 1 | 2 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 175.8533 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 212.4 | 11.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 23.2 | 5.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 232.2 | 25.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 44774.4 | 12.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 83.4 | 27.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 696.8 | 26.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 35985.6 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 27.2 | 6.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 142.4 | 17.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 198 | 19.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 201.6 | 16.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 820.8 | 22.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 225.6 | 18.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 82.8 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 263.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 276 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 56.4 | 18.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 140.4 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 166.6 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 184.8 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 77.4 | 25.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 190.4 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 481 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 59 | 11.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 104 | 20.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 764.1 | 28.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 966.9 | 29.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 7546.8 | 22.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 26.6 | 3.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 322.4 | 24.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 26275.2 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 40.5033 | 5.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 132 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 593.4 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 469.5 | 31.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 35.4 | 11.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 52.8 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 165.6 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 262.1967 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 856.4033 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 162 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 571.2 | 23.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 703.8 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 55.2 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 64.8 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 94.4 | 11.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 103.3533 | 14.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 124.2 | 13.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 126.4 | 15.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 141.6 | 11.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 28573.6 | 8.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3385.6333 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2707.8333 | 110 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 412.75 | 15 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 517.3 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1182.1167 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 480.35 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 564.3 | 19 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1097.2 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3646.0667 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1018.8 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 372.7499 | 315 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1504.1582 | 164.09 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2100.9893 | 91.88 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 552.7738 | 103.97 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1838.4613 | 105.76 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1396.9736 | 67.27 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1709.55 | 98.25 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 106.95 | 9 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1231.675 | 259.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1676.4 | 91.44 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16190.115 | 565.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.1499 | 81 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.383 | 17.79 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 64.5 | 10 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 551.8 | 124 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.8485 | 76.39 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61 | 60 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1201.1415 | 244.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1517.2498 | 315 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2485.75 | 815 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1828.4325 | 93.05 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4493.9998 | 315 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1404.8125 | 160.55 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7860.1015 | 319.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 107087.0996 | 654.3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1792 | 28 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2460 | 30 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 459 | 27 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.8333 | 50 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5741.6665 | 530 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4106.7 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1694 | 220 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4687 | 430 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1763.9999 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.65 | 137 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3288 | 144 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22105.2 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38886.9 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 863.8666 | 124 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8100 | 270 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 334.6 | 84 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86737.9 | 311 | 1 | 1 | 0892-Bottom ash clinker grinders | U3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119153.4497 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2734.1666 | 170 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 865.8333 | 50 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1123.3332 | 200 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4250 | 60 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2520 | 180 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 531.6666 | 116 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21369.6 | 371 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2730 | 195 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1304.9999 | 270 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1798.3333 | 32.5 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 650-Fluidized Bed
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 17.2 | 4.3 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 650-Fluidized Bed
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40158 | 230 | 1 | 1 | 0895-Ashpit trouble | U2-Forced - Delayed | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 264 | 11 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1251.8332 | 259 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16766.8 | 502 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | U1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36177.5 | 499 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1950.5766 | 323.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 326.6 | 284 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 679.46 | 339.73 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 48.455 | 8.81 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 928.3998 | 264 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 425.7 | 258 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15530.4 | 432 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10897.333 | 440 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6103.4998 | 585 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 934.1333 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1567.8 | 268 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 91.8667 | 10.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 258.75 | 11.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.2 | 51 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1218 | 290 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1187.3332 | 260 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16753.9165 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114404.55 | 507 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15680 | 560 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21888.2665 | 632 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 562.8332 | 307 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 187.8333 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102.9833 | 37 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1522.0665 | 289 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 406.8498 | 237 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 839.4999 | 219 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2164.983 | 539 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 868 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1853.8 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1695.3666 | 281 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1376.1 | 278 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1410.9331 | 296 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1698.6331 | 389 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52312.3496 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10197.7033 | 814.73 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2637.6931 | 335.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 415.6332 | 337 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7575.6 | 428 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14143.9997 | 480 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85317.2 | 526 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36513.75 | 535 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56814.75 | 855 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14282.2331 | 598 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3107.1131 | 335.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 918.3331 | 290 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 863.2998 | 291 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1152.1665 | 223 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 408.25 | 71 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6960.3331 | 380 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1640.45 | 301 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64193.5832 | 415 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5782.4 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1731.8666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.3 | 54 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1283.3333 | 110 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3059.9999 | 270 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3137.9165 | 443 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 103.125 | 9.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 135.375 | 9.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1038.1332 | 272 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1544.4 | 286 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1539.6666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2285.4665 | 244 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2692.9832 | 397 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7717.952 | 369.28 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1864.6499 | 279 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1256.0164 | 403 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1433.9332 | 274 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92764.0997 | 507 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 924.4999 | 129 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 333.9666 | 233 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.4666 | 71 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1268.4998 | 258 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42529.2 | 581 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.4 | 7 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 730.7788 | 246.33 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 901.3333 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 892.5 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 589.3333 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 488.75 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1090.8333 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2558.5 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 757.25 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 761.8 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1020.5 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1130.5 | 17 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234.3333 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.5 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10714.4999 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29488.4998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1037.5 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.625 | 53.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 376.064 | 144.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2450 | 490 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 37.0265 | 31.29 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3596.6666 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 22.3833 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 435.0833 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 954 | 318 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1700 | 425 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1900 | 475 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2505.9997 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2850 | 475 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 496.2667 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 775.5 | 110 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 275.3833 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1760 | 440 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1300 | 325 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 654 | 54.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1765 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2211.0666 | 161 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1960 | 490 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2325 | 465 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 975 | 325 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1272 | 318 | 1 | 7 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2125 | 425 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.5832 | 445 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1119 | 746 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22801 | 151 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2164.4998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2071.276 | 214.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189.156 | 114.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1152.2986 | 144.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5538.3333 | 100 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 650 | 325 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2100 | 420 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2325 | 465 | 1 | 10 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 109281.6663 | 532 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2173.1666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 955.2666 | 161 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1300 | 325 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2085.9997 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2520 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3800 | 475 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1095 | 365 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 316.2499 | 151.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31289 | 268 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 966 | 161 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2375 | 475 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2940 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 957.6664 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1554 | 37 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5097.71 | 70.9 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16835.8928 | 814.64 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.1667 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2042.3333 | 220 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3365.9998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 797.13 | 156.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 38.6833 | 11 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 812.5 | 325 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1083.3332 | 325 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1680 | 420 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1908 | 318 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2092.9999 | 420 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2200 | 440 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3725.26 | 64.9 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4474.6333 | 151 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7689.6664 | 340 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.448 | 73.82 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2845.8 | 108 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 105.8333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1721.25 | 405 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 78.3333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1614.6666 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 915.8333 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 5745 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 945.8333 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 5390 | 55 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 18.75 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 212.4999 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 295.6916 | 25.9 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 800-Miscellaneous
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 1204.35 | 93 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 47387.8666 | 293 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 966.95 | 233 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0934 | Bed material fan/blower motors | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 83.2999 | 102 | 1 | 1 | 0934-Bed material fan/blower motors | U1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 60.9 | 8.7 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 147.6 | 12.3 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 405 | 405 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 837.5 | 335 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 544.6667 | 34.4 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2081.9164 | 415 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 25785.3332 | 415 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 31.92 | 7.2 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 800-Miscellaneous
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 36.5 | 5 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0960 | Char transport piping and valves | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 421.2 | 31.2 | 1 | 1 | 0960-Char transport piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0960 | Char transport piping and valves | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 1459.57 | 4.2 | 1 | 1 | 0960-Char transport piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0980 | High pressure loop seal recirculation fans/blowers | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 328.5 | 73 | 1 | 1 | 0980-High pressure loop seal recirculation fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0980 | High pressure loop seal recirculation fans/blowers | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 3306.6666 | 160 | 1 | 1 | 0980-High pressure loop seal recirculation fans/blowers | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0982 | High pressure loop seal recirculation fan/blower controls | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 404.5 | 30 | 1 | 1 | 0982-High pressure loop seal recirculation fan/blower controls | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 283.5 | 16.2 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 91401.35 | 293 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 69.6 | 17.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 46.2 | 15.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 3585.9373 | 37.36 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 490 | 84 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 166.4 | 64 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2568.4166 | 85 | 1 | 1 | 0990-Refractory | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D3 | Forced - Postponed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 7492.5 | 90 | 1 | 1 | 0990-Refractory | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 58253.7165 | 241 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1393.6466 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 60.35 | 12.07 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 262.64 | 9.38 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 136.51 | 8.03 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 393.9 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1267.58 | 24.4 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 37531.7333 | 241 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 52915.9999 | 240 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 672.6 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1359.4867 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2717.3466 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | SERC | Summer | 3340.675 | 19.5 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 800-Miscellaneous
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1543.5 | 90 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296 | 148 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.0665 | 278.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1541.0805 | 23.51 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10380.6 | 711 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13108.6666 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11439.282 | 25.23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 449.2667 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 329.6333 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 184.975 | 75.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 8490.9 | 62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1129.333 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 72322.0495 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9128.1832 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18029.9665 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18815.1665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39550.194 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13974.2664 | 337 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20371.5 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27035.2832 | 259 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29914.4998 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31059.1665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37716.9329 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41429 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91927.5 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104859.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1547.2166 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12755.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13911.1 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22407.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23876.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64394.1658 | 1330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 25867.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 13838.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1077.02 | 47.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11237.3132 | 225.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12148.254 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 134726.1495 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 66599.9804 | 406.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3542.7499 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47672.5332 | 544 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47265 | 138 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 20908.9999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14156.9999 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23303.8497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5102.55 | 43.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14024.25 | 24.39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 683.8 | 26.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 704.776 | 47.62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 811.2 | 416 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1972.1 | 16.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 532.1 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1079.9999 | 324 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 655.5 | 437 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6874.1998 | 324 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 50.9999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 8856.2833 | 77 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 799.4 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11421.0832 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6464.8331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9627.55 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18100.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18866.0999 | 198 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20355.6665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43598.7998 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71445.8329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2307.1999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4930.7499 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17343 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17780.6666 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17855.7165 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18766.8663 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19282.5831 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19567.8331 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22812.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1281.9333 | 82 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19022.7699 | 264.45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20560.4997 | 405 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23291.8331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7357.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 43327.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 20444.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8451.6075 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11110 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12579.2333 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 21072.1498 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 46398.95 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2434.77 | 416.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 25650.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 75478 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1526 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24621.6664 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75110 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17412.2664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22834.5999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17282.4 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49564.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93205.7 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15803.7495 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26525.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29800.4 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 18544.9498 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2178 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6256.4 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176 | 88 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 600 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2072.3 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2137.8 | 84 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 451.6666 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 852.3 | 54 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1969.8 | 294 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3071.1208 | 32.47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15809.07 | 27.59 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 590.0417 | 8.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 735.6167 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 920.7667 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 26.25 | 3.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 688.5 | 15.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 74.6665 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23290.1066 | 50.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4473.3 | 62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 503.3333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 610.8333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148 | 148 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.78497 | 47.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2996.6666 | 58 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3424.35 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6600 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10489.5 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26670 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9737.5 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12271.5833 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17997.1664 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35840.9996 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38085.3332 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43939.7164 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50328.6 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 58346.5 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62863.4998 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12849.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18769.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21490.1166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34230.7 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100533.3329 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18284.9999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 31822.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40132.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 36581.7499 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 63898.8998 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9376.6833 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20369.2333 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 68377.5 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 75588.4 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 10015.8333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55301.9998 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33901 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36563.2997 | 762 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43629.1664 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48204.8332 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 59435.55 | 491 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10723.8497 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19066.6664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53386.65 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8602.98 | 225.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 170112.9 | 411 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69077.25 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215.004 | 28.29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1540.7 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1928.6667 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7180.8 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11810.4468 | 29.17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14978.88 | 20.16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4805.88 | 27.62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3985.282 | 34.44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10442.5657 | 25.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24075.84 | 32.36 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 335 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 877.8 | 26.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 462.15 | 11.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 518.5 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10905.0665 | 368 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 175680 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 4.1667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 96.2167 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 141 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 306.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19614.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20388.5831 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26020.2498 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42940.9851 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45390 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58541.5997 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3074.1666 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5174.5 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7581 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12195.8666 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19277.4662 | 652 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27083.9999 | 333 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30874.856 | 814.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46638.14 | 814.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76514.6666 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77150.5 | 469 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10357.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28204.5829 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45748.5606 | 813.79 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 94258.9664 | 659 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 31704.75 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 61020.8333 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 105446.7164 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 802.3575 | 17.85 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7937.6166 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7962.7166 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9460.7999 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9883.6833 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 14765.1 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 31673.7998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 57983.25 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 30816.75 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24534.758 | 565.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 461473.0496 | 1251 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67188.1164 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75033 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87391.5 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 43245.8546 | 645.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6383.2665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38070 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23628.6666 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1324.4 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1714.8 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2586 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5129 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21723.73 | 30.13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2060.8 | 34.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8291.86 | 23.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1092.9333 | 11.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 327 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 38.3332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 213.6667 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 483.6 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 8359.2 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6676.5499 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19582.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20614.67 | 216.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25677.5733 | 814.73 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50212.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70871.2663 | 532 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111234.7497 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6929.3333 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18550.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20013.75 | 593 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20438.5 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20831.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22436 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43752.8 | 728 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48390.75 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54607.5 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71175 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2743.4 | 116 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 22762.6665 | 440 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64158.8329 | 662 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64579.7 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 29752.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 33210 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 20647.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 21112.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 16207.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 41542.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8619.9998 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16095 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18126.1666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 222140.9164 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1647 | 61 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5318.5999 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10990.9332 | 448 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 41866.5 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 51010.4666 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5879.1664 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9441.25 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67028.4 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95482.5 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16297.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 78381 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7686.7665 | 458 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18905.7495 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46858.9995 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1681.3 | 43 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 118 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 314.1332 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1806.2 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2986.8 | 786 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1828.3 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3119.9833 | 32.75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8030.25 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 449.3667 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 559.1667 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1073.55 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 407.3333 | 9.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 515.4167 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 10.7333 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 124.8333 | 10 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3866.85 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7203.2666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9190.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12492.7999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15147.0332 | 529 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16578.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17442 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22488.3666 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23655 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34112.9163 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69902.2497 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5111 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7000.0832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27864.2148 | 264.45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39478.3665 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68628.8 | 472 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101441.9998 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 17595 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 19137.9165 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 22924 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 38269.9999 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 57066.25 | 355 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 73141.6 | 353 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10572 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14023.408 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 18288.7499 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22220 | 404 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 34444.7499 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 43101.4566 | 225.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 228384 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20473.1332 | 532 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21788.4662 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22465.35 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38474.2497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3868.3331 | 275 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17011.3366 | 216.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25287.0332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30104.9 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36771.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 30534 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53280.3332 | 302.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8200.52 | 18.68 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 625 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1366 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2428.4 | 23.35 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4438.08 | 29.44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7871.5616 | 33.19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8899.597 | 23.38 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11043.75 | 23.75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454.05 | 30.27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3073.4 | 24.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7400 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10349.3 | 24.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1081.7667 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1284.9167 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1153.875 | 15.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 263.9333 | 10.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 7312.9 | 62 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5530 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3108 | 37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32471.4562 | 260.78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46141.4 | 662 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47182 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4055.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10426.75 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13800.9 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18123.9165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21987.9998 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23123 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 25434.9331 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29414.6666 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31314.45 | 191 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49407 | 860 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64911.6 | 876 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65400.8329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107900 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2591.2832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4181.3332 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13657.8166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36192.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68437.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5355 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21888 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24552.7494 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 101997.4164 | 355 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2071.1666 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7748.052 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 10228.3828 | 178.87 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26333.0166 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 54461.25 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5532.5 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5114.8497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13294.05 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156692.7466 | 306.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37162.5332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91225.375 | 677.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26383.0832 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 13270.833 | 455 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52725.8663 | 487 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 88530.75 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12699.41 | 33.82 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 188 | 188 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335.2333 | 89 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6182.45 | 23.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3964 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5678.768 | 23.28 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 331.7 | 10.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 344.5 | 13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 757.0833 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 404.735 | 18.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 17386.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5953.5 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10570 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23015.25 | 477 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28704 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29694 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34156.9663 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38861.25 | 645 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20083.8 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21584 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23713.1665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29745.4329 | 626 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35079.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39577.9264 | 814.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76221.2498 | 525 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78517.7184 | 814.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17857.8666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18742.9666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24819.1665 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39677.94 | 493.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40121.8998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40232.8662 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42979.2996 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51568.85 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51770.4329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 70887.173 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102141.6661 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 33480 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30330 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 37612.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1754.9764 | 416.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10457.0999 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 44341.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3237.34 | 47.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 45014.8332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 46781.1666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 61416.2166 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 63108.4995 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 9744 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31275.5 | 355 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41955.083 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75394.0497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104487 | 870 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40498.4994 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84188.9994 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8093.7999 | 156 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45778.6498 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 50259.9998 | 525 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 281.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 28644.9999 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 18920.1666 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 438.85 | 13.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1152.3 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1399.075 | 29.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1177.0867 | 38.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 525 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 263.5 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 453.3333 | 17 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1617.0233 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 1570.4033 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 2283.9483 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 807.5 | 34 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 945.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1597.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2644.8216 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 341.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3157.7533 | 26.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 42.9 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 612.1567 | 13.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1071.0233 | 23.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 355.9933 | 13.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 578.88 | 13.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 658 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 16227.0499 | 213 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1010 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1285.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 877.1466 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2720.795 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 386.59 | 13.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2262.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 1348.095 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 1239.7466 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 627 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 2423.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3443.8 | 268 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 6405.75 | 70.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3466.08 | 21.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1330 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1211.75 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3073.07 | 42.9 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1155.35 | 21 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47928.3 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14186.0832 | 415 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54657.75 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11784.15 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3060 | 90 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 3685.11 | 42.9 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7835.85 | 99 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5051.081 | 74.39 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1625 | 25 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 800-Miscellaneous
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1142.9 | 11 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 3024.5 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 455.7667 | 22 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 85391.7398 | 509.7 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 4432.6666 | 40 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 261.175 | 9.3 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 319.7 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1457.8167 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8260.3 | 102 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38244.5 | 446 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 220.4167 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 560.4333 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2487.7333 | 38 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 220.4167 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 918.6667 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1430 | 40 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 582.6667 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 639.7833 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 76.5 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 81940.2 | 222 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 108000 | 75 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1085.9833 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 653.1 | 21 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16032.4999 | 330 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 321.2333 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 538.2 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1054.9 | 154 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17000.4998 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 691.6 | 39 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2885.4525 | 17.85 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 480 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1052.3333 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 511.6667 | 20 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 206.9533 | 14.8 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1463.9333 | 14 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 87.1 | 40.2 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 24126.6666 | 154 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39525.5664 | 746 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15623.1363 | 175.18 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46554.4665 | 554 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 13706.7 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3851.3333 | 20 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22947.6998 | 579 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33302.083 | 575 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45961.4996 | 585 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63037 | 746 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6013.3332 | 164 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 22075.083 | 455 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 27669.6 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 471.7 | 53 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3672 | 48 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 890.1666 | 245 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1229.01 | 409.67 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 307035.0663 | 175.18 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 601.9133 | 22.6 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33724.5996 | 546 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34700.2496 | 585 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 572.1383 | 9.7 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22153.1833 | 193 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136325 | 1330 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37367.3333 | 115 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50689.7843 | 814.73 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27388.4 | 184 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21453.5 | 535 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 7380.5832 | 155 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 7451.9666 | 293 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 102.8333 | 61.7 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 100.52 | 107.7 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 122.5616 | 48.7 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 15420.5333 | 154 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10115.8499 | 153 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96777.45 | 627 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9648.1 | 179 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47755.4998 | 585 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10423.7666 | 179 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25721.0831 | 395 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16919.1 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9347.65 | 197 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 437.1833 | 17 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13998.9333 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 772.35 | 19 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1997.4616 | 31.3 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 800-Miscellaneous
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28851.6781 | 810.82 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47770.8111 | 810.82 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49272.1424 | 814.64 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4749.2 | 766 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 439 | 439 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 947 | 473.5 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105894 | 555 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129375 | 500 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42267.6 | 531 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41910 | 635 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50715 | 345 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 194257.4998 | 450 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30481 | 340 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40481.25 | 635 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 138145 | 350 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 709.1333 | 22 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53840.0739 | 814.73 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98743.3332 | 550 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101859.3331 | 598 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88074.4663 | 553 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40811.5832 | 535 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20042.9997 | 459 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67409.6664 | 860 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69863.0975 | 814.73 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54806.6998 | 304.2 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 55478.5 | 655 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31268.5998 | 699 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145252.7999 | 432 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200 | 200 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 967.2 | 78 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47091.3141 | 813.79 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58125.4996 | 606 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130619.7995 | 699 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101902.5 | 450 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 14056.7833 | 229 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4197 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7116.6663 | 610 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8796.4999 | 219 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40609.9998 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 228073.7597 | 509.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 8907.739 | 46.29 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 527 | 17 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48300 | 300 | 2 | 2 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30382.4999 | 225 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38535.1165 | 593 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7506.1666 | 290 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8120 | 200 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31800.9998 | 330 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6982.5 | 38 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8289.4 | 93 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 98579.7 | 522 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7600.3333 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17772.3333 | 220 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1208.169 | 46.29 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 863.1 | 126 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15049.0332 | 478 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24089.8498 | 459 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28429.9166 | 115 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5189.3332 | 280 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44562.5831 | 553 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66126.0998 | 249 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 2717.6648 | 63.77 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20692 | 280 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1068.75 | 19 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 573.4667 | 17 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65294.1661 | 850 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 72548 | 560 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29744.0245 | 813.79 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3602.0833 | 95 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 138324.0848 | 509.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28348 | 373 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62050 | 340 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29843.7332 | 352 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 398.3333 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 575.6667 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 58.8333 | 10 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26967.6664 | 340 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14869.9998 | 600 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 31159.9996 | 570 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 148.8 | 93 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12232.9997 | 390 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 7449.604 | 46.29 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17498.8497 | 387 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25474.5 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25883.3332 | 125 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10465 | 455 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141578.2497 | 495 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 72607.4995 | 675 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 11224 | 244 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8267.9999 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33669.3332 | 535 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59171.4165 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11707.6833 | 181 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25298.4998 | 570 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5861.4998 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4834.05 | 201 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5271.8333 | 235 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51582.3 | 609 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 64548.1663 | 610 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149675.24 | 152.8 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33006.4968 | 814.64 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125035.1664 | 770 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4609.4999 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6057 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11800.9166 | 216.2 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140802.3997 | 876 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27060 | 330 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2739.6 | 27 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61706.1462 | 662.32 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 500423 | 770 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4354.2 | 164 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31904.2499 | 315 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44968.128 | 814.64 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61833.6464 | 700.4 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12896.6666 | 200 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 15894.6665 | 524 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13.95 | 93 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21351 | 330 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1257.12 | 24.3 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2683.9583 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2361.6666 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 124.6 | 17.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 280.9533 | 14.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 399.6 | 10.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 606.97 | 13.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 1469.3933 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 79.2 | 19.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 399.2167 | 17 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 270 | 10.8 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 1568.245 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 51681.0832 | 349 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 3934.2333 | 13 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 4236.8667 | 14 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 820 | 164 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3337.6665 | 190 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2093.4499 | 447 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 568.3333 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1031.1 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 140.1833 | 13 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 634.5 | 27 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66874.1665 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71173.9498 | 639 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35547.5 | 590 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164021.55 | 847 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2080.5333 | 47 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 807.95 | 39 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 112907.9834 | 932.61 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46464.4996 | 570 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100641.3329 | 1315 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.8 | 6 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 838 | 167.6 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 279.1666 | 335 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 642.5666 | 37 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 602.3667 | 17 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 667.1 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 842.0667 | 17 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4247.0498 | 303 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17229.45 | 269 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57850 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21261.3331 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34216 | 658 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12853.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25761.6665 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34485.5 | 590 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 58059.4997 | 453 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12005.3331 | 320 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31294.9998 | 300 | 2 | 2 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42896.65 | 548.2 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3721.4495 | 789 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6352.3333 | 190 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6033.3 | 507 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61364.333 | 476 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 357.825 | 11.7 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1133.3 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19615.1663 | 595 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1497.2466 | 120.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9792 | 255 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 16053.9165 | 455 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1782.6666 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270379.9996 | 1320 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16473 | 380 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19976.2498 | 315 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 20779.1665 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 21903 | 210 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 251.85 | 23 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 908.6 | 21 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7737.945 | 25.05 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19692.7498 | 495 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30922.5 | 570 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195288.3329 | 1330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15190.5 | 570 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9465.8816 | 120.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50537.5 | 650 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 63854.6663 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 36475.7766 | 326.6 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43026.75 | 585 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55888.4994 | 855 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3156.3 | 167 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15960.4164 | 815 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 501.2333 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 939.7667 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39636 | 270 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19670.5498 | 639 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22863.4999 | 330 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29121.75 | 315 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47687.0331 | 553 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55963.6 | 644 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 119953.9993 | 1110 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5462.0999 | 162 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1287 | 39 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 15107.9332 | 236 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1844.25 | 45 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49797 | 495 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19884.1665 | 223 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 152761.5 | 747 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267098.4158 | 1315 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6810.8166 | 167 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 6 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 324.8333 | 10 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20709 | 270 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38080.4829 | 593 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68827.5 | 665 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3933.3332 | 200 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8800 | 550 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20175.75 | 245 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191858.9662 | 634 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1348.05 | 47.3 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10541.6665 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8060.5 | 147 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4456.1166 | 167 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126064.9996 | 570 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 676.5332 | 472 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 313.3333 | 10 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4784.513 | 565.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8837.3999 | 198 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35315.8 | 611 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37542.5632 | 548.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3091.6666 | 140 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15356.8498 | 333 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41835.2832 | 379 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9680.4332 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7712.5 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18120.8332 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 19450 | 250 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 836.1999 | 444 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 991.1 | 22 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 903.0232 | 236.6 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 362.5 | 10 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1757.4998 | 570 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7862.36 | 25.05 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11848.263 | 565.1 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19368 | 269 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56088.6664 | 707 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62608.8171 | 810.82 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73738.5 | 654 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69255.9996 | 528 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 121310.9164 | 659 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2180 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34342.4994 | 855 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28389.5496 | 609 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 39746 | 280 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 47267.4998 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1210.8 | 18 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 730 | 40 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 392.3333 | 20 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 7530.425 | 25.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37592 | 635 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2593.3333 | 50 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1612.1666 | 170 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15953.6665 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18825.5166 | 269 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36722 | 860 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67360.9831 | 691 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20520 | 855 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 48978.2995 | 747 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25590.9331 | 416 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37505.9994 | 855 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35763 | 420 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.25 | 15 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28498.8224 | 814.64 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33157.8498 | 627 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57562.0831 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78328.8 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4276.5332 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10659 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6025.9166 | 167 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 624.1667 | 50 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18222.6665 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23157.0331 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34077.7329 | 593 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61336.7496 | 555 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13558.1166 | 113 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 44304.2 | 338.2 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48865.2162 | 691 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9108.8331 | 410 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5058.9331 | 311 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55520.8329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109035.3 | 627 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42504 | 644 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55120 | 1300 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 37762.4997 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 48854.9997 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 83885.4 | 522 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60343.9996 | 570 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10250.535 | 120.1 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9705.8498 | 231 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6787 | 220 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8281 | 245 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12279.6 | 324 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 28349.2 | 88 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15977.75 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17530.6665 | 380 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 42344.1663 | 610 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55452.8332 | 406 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 104867.7328 | 824 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16365.9999 | 210 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72037.9831 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 147364 | 560 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160352.5 | 770 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10155.0165 | 193 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11079.75 | 395 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30315.7662 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48408.1 | 598 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110760.4996 | 570 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13583.7 | 486 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26085.15 | 637 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55039.2662 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226430.5497 | 783 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 44078.65 | 749 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57376.0331 | 691 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76488.6664 | 680 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11829.2666 | 191 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10450 | 275 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13017.5332 | 478 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59354.0162 | 739 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34605.5832 | 535 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36951 | 565 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52539.9996 | 555 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 149680 | 120 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11034.45 | 93 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6225.45 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79248 | 320 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16311.54 | 164.1 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17923.5 | 315 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61240 | 800 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27846 | 585 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 41469.8331 | 610 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2944.0666 | 158 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20400.6204 | 206.31 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87261.6665 | 410 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65956.5832 | 535 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28243.5 | 190 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5582.1999 | 156 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22488.25 | 115 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27134.05 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28578.3329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 90635.0915 | 466.67 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34891 | 820 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41424.75 | 855 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 361150 | 500 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 10839.1999 | 204 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 800-Miscellaneous
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 55665.5 | 349 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16967 | 380 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6781.65 | 46.77 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 199394.2 | 404 | 1 | 1 | 1070-Second reheater | SF-Startup Failure | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41156.9997 | 459 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23584.5832 | 535 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135026.6658 | 1300 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1917.6667 | 44 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17656.5 | 395 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52326.3997 | 876 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98691.3328 | 740 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1005 | 20 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16986 | 380 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30482.0832 | 245 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9499.9999 | 120 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2579.25 | 285 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17636.75 | 395 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43616 | 752 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62777.05 | 581 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 220.8333 | 106 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 650-Fluidized Bed
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 50438.9999 | 180 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 650-Fluidized Bed
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 818.3333 | 20 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 800-Miscellaneous
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.15 | 51 | 1 | 1 | 1075-External reheater link tubing | D1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 287.4666 | 176 | 1 | 1 | 1075-External reheater link tubing | D1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162.5333 | 46 | 1 | 1 | 1075-External reheater link tubing | D1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49170.4998 | 645 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 561.85 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11732.4998 | 570 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23949.9996 | 600 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33784.1661 | 810.82 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62458.3825 | 813.79 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12263.5997 | 516 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65533.3328 | 800 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5115.6 | 116 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8304.9 | 93 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 161199.9997 | 750 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3755.8333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3918.3333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2310.1666 | 167 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 7070.5832 | 155 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 389.6 | 9.6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 798.4333 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 33.8333 | 10 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21298.6665 | 560 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48330.0996 | 546 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7389.2 | 116 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18834.6665 | 560 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48162.708 | 810.82 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17514.1164 | 427 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8409.95 | 326.6 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1876.9866 | 47.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5628 | 90 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44834.1663 | 550 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.8333 | 65 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 493 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3773.3333 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15708 | 510 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137763.3328 | 740 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51803.5 | 410 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 235.6 | 93 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2373.6717 | 47.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 4868.5 | 107 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4536.5666 | 58 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6986.1666 | 167 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1378.6667 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 243.6167 | 9.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 383.35 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1845.69 | 30.6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 121.3333 | 10 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6063.75 | 245 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3480 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 96.1 | 93 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14707.8 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 23971.3332 | 164 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1810.8333 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7219.9666 | 167 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30883.3332 | 340 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1156.54 | 300.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2800.7333 | 43 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 252.3317 | 10.1 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 907.6667 | 35 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19470.4164 | 415 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26188.5 | 510 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 53401.1332 | 164 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5802.6666 | 136 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2966.6667 | 50 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119042 | 773 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1406.3 | 42 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53212.1331 | 616 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2155.3333 | 40 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2090.7167 | 47 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 560.15 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 810.9 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 793.3333 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 325.8333 | 10 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23444.4166 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 53181.8331 | 610 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57386.1064 | 700.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63691.5998 | 552 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14485.333 | 560 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12233.1666 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33993.7663 | 502 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87308.9998 | 270 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104146.6664 | 800 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8795.5 | 98 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1692.9066 | 47.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4352.4 | 93 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3261.5333 | 58 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113991.7497 | 783 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 120486 | 516 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31435.9999 | 174 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39946.9997 | 516 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 207.4 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 232.4233 | 9.8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1053.8 | 33 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5782.6 | 58 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22552.88 | 700.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 19198.7333 | 244 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4489.8 | 42 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 174.125 | 10.5 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8864.6132 | 236.6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1068.3 | 27 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6917.7499 | 201 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15655.1666 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21177.5831 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32623.4996 | 585 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51997.3328 | 740 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32375.2786 | 813.79 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 32933.9332 | 164 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 9246.3 | 98 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17098 | 415 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26118.4 | 448 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48264.75 | 855 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5711.9999 | 90 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 197085.3997 | 876 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1183.125 | 37.5 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 953.775 | 24.3 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | WECC | Off-Peak | 1177.5893 | 33.92 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 939.7333 | 32 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 670.65 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 4750 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 369.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 297.5 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 286 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 1360.1816 | 25.9 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 28426.05 | 349 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 32193.1665 | 419 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 38476.5166 | 347 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 30143.7497 | 525 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2982.4666 | 308 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 6120.3331 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 5730 | 300 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 4880 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 48054.9999 | 300 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 43219.9998 | 300 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 67249.9998 | 300 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 10580.9999 | 180 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 611.3332 | 280 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74 | 74 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 488.2499 | 135 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 600 | 100 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 519.1667 | 10 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13702.6331 | 586 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90220.2666 | 278 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23613.3329 | 575 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25624.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34481.61 | 654.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50050.8331 | 850 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72417.2164 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87807.5 | 682 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 6526 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67364.4998 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108564.3 | 309.3 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 768.5 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 180134.5 | 111 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1722.5 | 53 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8444.3333 | 55 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4223.3332 | 280 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68796 | 637 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40658.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44274.1996 | 579 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47947.333 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58724 | 530 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67036.6658 | 1300 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4370.8 | 56 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 59461.133 | 494 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3557.3333 | 232 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1161 | 290.25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 699.5675 | 91.05 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 807.3333 | 28 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13365 | 220 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73123.9996 | 606 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103411 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13144.3333 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21029.1666 | 245 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52533.6662 | 718 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 57868.8 | 411 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 4705.6333 | 43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76617.4996 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24055.5 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576 | 192 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 6546.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 684 | 12 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1488 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1668 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6792.6833 | 79 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 109185.05 | 69.7 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6098.8333 | 86 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26597.3331 | 320 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30006.6 | 156 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105140.8828 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168984.5332 | 544 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51241.6664 | 325 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 29264.9999 | 450 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1340 | 30 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 82816.2 | 417 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2479.1667 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20938 | 232 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2329 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40936 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.85 | 47 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.99 | 57.33 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 914.6666 | 70 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2450 | 500 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18640.8 | 144 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2997.6666 | 85 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10260.2499 | 105 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37298.2997 | 507 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14420.8162 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22765.2 | 244 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24675.0333 | 106 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 46432.75 | 785 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 5112.5 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3741.5 | 105 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2475 | 450 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 30020.6833 | 127 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31597.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37779.6664 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124888.4 | 728 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7012.5 | 165 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31478.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57827.3829 | 593 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3766.5466 | 336.8 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 11948.75 | 605 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 14642.6665 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 423.5833 | 115 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 352.3666 | 31 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1535 | 50 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3071.3333 | 85 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16799.6663 | 505 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12557.3332 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28560.4199 | 359.1 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80221.1664 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 115365.4665 | 494 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12201.705 | 127.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19550.6665 | 440 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58681.5 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93252 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116080.5 | 570 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7479.6665 | 190 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182.5833 | 35 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1128.75 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 82742.15 | 34.7 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45434.2499 | 405 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 79678.9998 | 654 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 38241.8432 | 416.2 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 25112.5333 | 208 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1842.953 | 63.77 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 4308.7263 | 63.77 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26339.5833 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214262.7164 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5438.6499 | 123 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19000 | 760 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 65652.6 | 494 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 990 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 439.0833 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1866.0416 | 32.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1318.1666 | 55 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 84.3 | 18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 726.9 | 18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 6231.1331 | 293 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 484.1833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 829.6667 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 39.6667 | 14 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 726.75 | 17 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 792.75 | 21 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 514.6667 | 32 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3359.1 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1011.4333 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 696.35 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 744.8 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 911 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1157.7333 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 502.1333 | 14 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 690 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1758.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1211.6667 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1178.9166 | 43 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 27.8667 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 384.75 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 686.1 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 777.4167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1839.5167 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 660 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1008 | 21 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 907.25 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 972 | 24 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 981.9833 | 19 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 8691.7333 | 68.8 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1604.6333 | 23 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 264.1333 | 5.6 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 569.2 | 142.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24348.75 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 28868.25 | 183 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2367.4999 | 150 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 480 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 245951.5333 | 28 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 603.4 | 3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41097 | 532 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19626.4998 | 510 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1292.715 | 37.47 | 2 | 2 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124.6666 | 55 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19361 | 380 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9362 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20685.5 | 110 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1569.7499 | 315 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1220 | 20 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1544.6666 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 51933.4665 | 196 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1019.1 | 158 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28219.9998 | 300 | 2 | 2 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8669.9166 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 466.55 | 133.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1200.8 | 48 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 194.5 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 872.0833 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10494.5 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28438.3333 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34609.9998 | 300 | 2 | 2 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.5 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 635.5 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71610 | 825 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 138384 | 93 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13944.85 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5573.7333 | 68 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1886.25 | 45 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7334.1664 | 650 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1540.425 | 28.5 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102246.1663 | 610 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 55079.9499 | 183 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11130 | 300 | 2 | 2 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19823.7833 | 151 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.75733 | 0.64 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 153.75 | 45 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1913.3 | 19 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 342.3925 | 4.53 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1460.8 | 6 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 16025 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 486.35 | 13.7 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2185.3333 | 40 | 1 | 1 | 1105-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19424.1665 | 650 | 1 | 1 | 1105-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 19416.6666 | 25 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 398.5583 | 16.9 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 2780.435 | 11.9 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24206.9165 | 395 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.8333 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.3333 | 100 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17969 | 151 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23903.3 | 151 | 1 | 1 | 1140-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48666.1264 | 700.4 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 843.3332 | 200 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3333 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 50 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5522.9999 | 315 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.56 | 4.64 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1260 | 315 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9097.75 | 151 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1522.4999 | 315 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1890 | 315 | 1 | 2 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.5833 | 23 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2600 | 520 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27 | 5.4 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1803.1665 | 310 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1854.8332 | 310 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540.9 | 60.1 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2064.9999 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78724.9998 | 564 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4340 | 620 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4685.5832 | 295 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.0832 | 245 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1575 | 315 | 1 | 3 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37245.4331 | 598 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1137.645 | 24.3 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 650-Fluidized Bed
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.0467 | 19.4 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 62940 | 60 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57.75 | 21 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.4895 | 13.13 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1324.3999 | 258 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1823.1998 | 258 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.346 | 32.84 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.848 | 11.16 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.5252 | 13.43 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2015 | 325 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3173.0666 | 326 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23487.1997 | 471 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.1637 | 20.42 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.5733 | 21.04 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.4387 | 8.78 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.0707 | 14.36 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.0215 | 20.01 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 34496 | 49 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1007.9165 | 295 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11037.0998 | 471 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1212.75 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 7104 | 32 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2118.3997 | 384 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 609.5833 | 55 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37154.8798 | 359.1 | 1 | 1 | 1170-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500 | 60 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.1383 | 6.79 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2075.7 | 11.1 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2664.6666 | 40 | 1 | 1 | 1180-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67000 | 670 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1877.1999 | 148.2 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.8397 | 12.02 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 140 | 20 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87344.9898 | 493.8 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 284.75 | 17 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 432.15 | 13.4 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 562 | 20 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168.3333 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1743.3833 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11904 | 16 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60515 | 380 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1552.5666 | 94 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2394 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1772.9135 | 313.79 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 959.8667 | 8 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34212.5 | 69 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 211.0966 | 76.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 683.1 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5313.3833 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16524 | 306 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 881.65 | 21 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11130.85 | 69 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22135.6117 | 47.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 476 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1741.1 | 69 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 280 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217 | 108.5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 522.855 | 24.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 652.05 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8.0166 | 37 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 336 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.8666 | 49 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1193.4998 | 330 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2607 | 330 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190.6666 | 130 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 251.3333 | 8 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 394.35 | 99 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1727.05 | 13 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2064 | 344 | 2 | 2 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1900.1337 | 21.14 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2193.75 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2531.25 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1634.375 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 1593.75 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204.75 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1104.5833 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10615 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 306.6666 | 115 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560.4167 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9445.4833 | 53 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2270 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4212 | 108 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 291.6667 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 421.1667 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1221 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1336.4167 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2824.5 | 269 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4799.3333 | 40 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.96663 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15048 | 57 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15477.3333 | 32 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24680 | 48 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1593.7267 | 12.2 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 463.25 | 85 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5036.25 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 509.25 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 615.3333 | 65 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40 | 50 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3101.0166 | 43 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6367.5 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12550 | 50 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1362 | 227 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.6 | 18 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 674.3333 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 900.8333 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4106.6666 | 140 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1897.5 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21615.1666 | 53 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 227.5 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18806.5 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.2 | 24 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 576.6667 | 10 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3234 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.9166 | 115 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5735 | 185 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23630.9333 | 53 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1740 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 257.6667 | 10 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2240 | 140 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4584 | 191 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5500 | 100 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8984.25 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12330.3667 | 38 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.3333 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133.8333 | 55 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4446 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4762.5 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6236.25 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6446.4167 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2000.25 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4310.0333 | 43 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2172.75 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 990 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2828.1 | 33 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3930.9166 | 215 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4860.4167 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5075 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20283.3167 | 23 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 669 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10838.5 | 53 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 150 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472.5 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 570 | 190 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1798.5 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3462 | 20 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3574.9999 | 150 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.25 | 75 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 834.5833 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1800 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5563.5 | 45 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.85 | 67 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385 | 35 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2784 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3197.7333 | 58 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860 | 430 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 602 | 430 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5663.6666 | 260 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8413.1999 | 162 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | U1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3281.3332 | 460 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 709.9998 | 300 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3347.833 | 530 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7310 | 680 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 637.9999 | 330 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5598.6664 | 680 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1300 | Water side fouling | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 150 | 1 | 1 | 1300-Water side fouling | D1-Forced - Immediate | 100-Fossil-Steam
1300 | Water side fouling | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 55205.1999 | 237 | 1 | 1 | 1300-Water side fouling | U2-Forced - Delayed | 852-CC steam units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 218.05 | 147 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 851-CC GT units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 399.4998 | 255 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 852-CC steam units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 116830.9333 | 56 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 852-CC steam units
1310 | Water side cleaning (acid cleaning) | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6138 | 110 | 1 | 1 | 1310-Water side cleaning (acid cleaning) | U1-Forced - Immediate | 100-Fossil-Steam
1320 | Tube supports/attachments | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7267.9232 | 216.2 | 1 | 1 | 1320-Tube supports/attachments | U2-Forced - Delayed | 100-Fossil-Steam
1320 | Tube supports/attachments | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Summer | 686.1333 | 166 | 1 | 1 | 1320-Tube supports/attachments | U1-Forced - Immediate | 861-CoG GT units
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12168 | 169 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 3726.25 | 75 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U2-Forced - Delayed | 851-CC GT units
1340 | Tube modifications (including addition and removal of tubes) | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1887.9667 | 38 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U2-Forced - Delayed | 852-CC steam units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 256199.76 | 55.89 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4825.6 | 416 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7176 | 416 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 968.8 | 112 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14830.4 | 416 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59 | 15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88377.3 | 237 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 938.6 | 19 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 510.4667 | 19 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 33081.5333 | 247 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 37037.6666 | 230 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2020 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 17657.8999 | 102 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | SF-Startup Failure | 861-CoG GT units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 78.5333 | 19 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 862-CoG steam units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 9175.1833 | 53 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 862-CoG steam units
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 679.3999 | 258 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1513.05 | 99 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1526.8499 | 243 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 7717.6999 | 213 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16822.6664 | 740 | 1 | 1 | 1360-Boiler drains system | U2-Forced - Delayed | 100-Fossil-Steam
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 13027.3366 | 229.22 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 38474.577 | 229.22 | 1 | 1 | 1360-Boiler drains system | U2-Forced - Delayed | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1972.5949 | 117.3 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84.2667 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 489.92 | 15.31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 873.9499 | 231 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97350 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 55362.5 | 430 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36.2667 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 250.6 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 285.6 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 544.9333 | 244 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2153.9833 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 66050.4 | 146 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 197158.5 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7401.85 | 111 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9504 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 86724 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 139 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.05 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40028.4333 | 46 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.5 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15716.6664 | 460 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 479.1875 | 10.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 685.9999 | 294 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 26888.4 | 198 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 230.85 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 792.0625 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 991.1665 | 190 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2796.5667 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6334.2 | 391 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9374.3667 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16274.7 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 208093.2 | 42 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.25 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.5833 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12796.6666 | 200 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 607.5998 | 294 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2311.1 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56.1167 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 129.8333 | 205 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 57986.9333 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1541.75 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 72072 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93407.2665 | 446 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.5 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266.9 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1050.75 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4086.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 116.5333 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1008.2 | 28.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2139.9 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 5182.3333 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 12352.0833 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 34801.8333 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 235987.6 | 152 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 83.3333 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 280.5 | 99 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 541.3333 | 145 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18196.2 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 38187.5999 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 183196.1999 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3332 | 140 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7519.9998 | 600 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 396 | 528 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2385.45 | 93 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.6 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 173.2 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 754.5998 | 231 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5413.1 | 114 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.6666 | 70 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4940 | 152 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 968.9333 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2409.1667 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20184.5 | 70 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 43.05 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 396.9 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1547.8833 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 146.5708 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 76032 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2011.6832 | 301 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 398.25 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 676.3999 | 267 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5111.9999 | 270 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 207 | 69 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1240.3833 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 41.8 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 127.8 | 18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 157.0833 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4835.3875 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6796.6332 | 158 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 796.7 | 257 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 440 | 440 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 960.7667 | 38 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4561.6666 | 119 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.1667 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.3333 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 295.5 | 197 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428.75 | 245 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1512.8 | 496 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4272.8833 | 41 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4655.1667 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2802.8 | 56 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 206.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 9787.9833 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 13484.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 82.5 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 129.5 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 130 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 156.8 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 618.8 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 846.075 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1975.1417 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 721.6 | 328 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 17.5 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 735 | 105 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 69587.1 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45490.8 | 668 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 189.9499 | 393 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18176.173 | 178.87 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.75 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171.3332 | 257 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 510 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4164.3332 | 260 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 409.5 | 11.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2692.3332 | 197 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13618.7331 | 308 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1146.6 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1388.7375 | 7.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26758 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 52242.3 | 198 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 193676.9999 | 198 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7558.8331 | 682 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 5915.3833 | 97 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 650-Fluidized Bed
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 440 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 598.3516 | 31.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 59.5333 | 19 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2346.5 | 39 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2688.4 | 39 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11712.6667 | 20 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1578.5833 | 95 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2755.2 | 336 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5915 | 60 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5.7 | 9 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1321.6666 | 260 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 27 | 54 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1928.1999 | 372 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 209.15 | 89 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 12580.75 | 455 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.8666 | 76 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 385.9499 | 279 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1972.9166 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 870.4625 | 41.95 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 555.3332 | 245 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.8333 | 38 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6349.9998 | 600 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 765 | 85 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1586.0248 | 359.1 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 231.2616 | 127.3 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 30 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 151.25 | 5 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 705.7664 | 683 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 85.0666 | 116 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 808.25 | 265 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3024 | 336 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 458.3333 | 100 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6353.4328 | 746 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1835.3998 | 684 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2778.75 | 585 | 1 | 1 | 1401-Forced draft fan dampers | U2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2763.75 | 335 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8059.9999 | 195 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4635.4 | 308 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 153.75 | 25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1783.4 | 241 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 52 | 26 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 313.6583 | 28.3 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1065 | 355 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11644.183 | 431 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1023.4998 | 345 | 1 | 1 | 1407-Forced draft fan lubrication system | D3-Forced - Postponed | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1552.5 | 345 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.45 | 57 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9975.75 | 849 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1658.3166 | 73 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113440.1665 | 410 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2674.9999 | 150 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.2 | 4.4 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 621339.9996 | 564 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 45 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2912.6666 | 170 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 855 | 150 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4195.6 | 136 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1824 | 96 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 37895.517 | 497.97 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2121.3499 | 231 | 1 | 1 | 1410-Forced draft fan motors | U3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 860 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1438.2 | 36 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9814.4877 | 48.02 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5410.45 | 449 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 14225.8165 | 449 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22.3667 | 11 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 718.06 | 4.46 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 5.54 | 22.16 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.85 | 21 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 225.75 | 45 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 540 | 90 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1395 | 450 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10079.3333 | 40 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2082.4999 | 210 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 185 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1687.8333 | 41 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5739.3498 | 237 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 261 | 522 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 27178.3333 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32532.5 | 65 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5904 | 492 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 895.0499 | 243 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 333.99 | 111.33 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11794.9998 | 300 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5021.2499 | 225 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 26319.3332 | 194 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.3333 | 4 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2274 | 758 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 80.5147 | 22.16 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22.58 | 225.8 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3507 | 36 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1969.8 | 84 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2674.88 | 102.88 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3514.5 | 106.5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19781.75 | 335 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8489.6175 | 266.55 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 34230.8333 | 50 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3422.4 | 28.52 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 20496.7 | 658 | 1 | 1 | 1410-Forced draft fan motors | U2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 16524 | 136 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 40290.2497 | 429 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 11.4 | 18 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 650-Fluidized Bed
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2542.8 | 72 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227 | 113.5 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1364.02 | 97.43 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5591.78 | 90.19 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2481.2497 | 375 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10481.6666 | 100 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17263.4 | 308 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 323.75 | 185 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1343.25 | 6.75 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11972 | 410 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276 | 92 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2451.8663 | 568 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3142.96 | 92.44 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.96 | 6.44 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 911 | 91.1 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2057.1599 | 142.2 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5261.6666 | 308 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237 | 9.48 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 342 | 5.7 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.7332 | 128 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 212 | 106 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1173.5666 | 323 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 5822.0828 | 785 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1749.6 | 97.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10226.6665 | 650 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 835.2 | 104.4 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15.5 | 3 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1496.6666 | 200 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 737.4997 | 375 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16949.9999 | 225 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13411.65 | 371 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1196.8 | 35.2 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 758.8331 | 314 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1115.88 | 30.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1062.9 | 118.1 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.7123 | 5.18 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3493.7497 | 375 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18583.6328 | 758 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 796.4 | 72.4 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 950.4 | 17.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 316.8665 | 196 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267 | 133.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 578 | 115.6 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14771.9831 | 371 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2166.3331 | 335 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | WECC | Summer | 384.992 | 33.92 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 650-Fluidized Bed
1412 | Forced draft fan drives (other than motor) | HRSG Boiler | HRSG Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 165.6 | 72 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | SF-Startup Failure | 852-CC steam units
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 72.2499 | 255 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14717.8328 | 758 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2846.25 | 49.5 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 250.5 | 90 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70550.8332 | 155 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5283.45 | 531 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10882.0833 | 65 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141063.8 | 758 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 725.3332 | 256 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 82.8 | 13.8 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 800-Miscellaneous
1413 | Forced draft fan couplings | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 532.5 | 213 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 800-Miscellaneous
1413 | Forced draft fan couplings | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 179.4 | 13.8 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 800-Miscellaneous
1413 | Forced draft fan couplings | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 331.8 | 15.8 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 800-Miscellaneous
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3260 | 50 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11839.3333 | 28 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1430.8998 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5904 | 246 | 1 | 2 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 502.3332 | 274 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1106.35 | 203 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2617.1999 | 216 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2274.9997 | 750 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1479 | 123.25 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343.5833 | 35 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 911.1665 | 248.5 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1455.4998 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15.2933 | 5.92 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 661.9333 | 4 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 569.6 | 89 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1512.42 | 22.16 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 551.1333 | 14 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3519.6333 | 29 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1377.6 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3345.6 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 99.6666 | 230 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 541.7999 | 189 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1240.7167 | 29 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.3998 | 246 | 1 | 3 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 447.3 | 126 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4576.4999 | 243 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8655 | 20 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6083.333 | 500 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 35.3333 | 20 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 280.98 | 46.83 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.6667 | 50 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191 | 95.5 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278.1 | 27 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 706.4998 | 270 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 83.8716 | 55.3 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 598.5 | 133 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2090 | 475 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 445.8332 | 535 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1460.3333 | 52 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 651.9 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9641.6665 | 500 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 568.8666 | 106 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.1998 | 243 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1239.3 | 243 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4456.6998 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 696.5932 | 141.68 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1448.6665 | 410 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3173.5 | 33 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.4999 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1070.1 | 246 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2510.0331 | 586 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4551.2663 | 586 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.3667 | 2 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2414.55 | 160.97 | 2 | 2 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6623.4 | 116.2 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3244.9998 | 300 | 2 | 2 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1068.75 | 855 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 461.6666 | 100 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1639.7333 | 208 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 991.1665 | 313 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278800.2328 | 842 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 163.7999 | 108 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7590 | 276 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.66667 | 1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 199.4333 | 193 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 673.6665 | 470 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 475.9999 | 120 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1388.3332 | 340 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.5 | 330 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 273.69 | 91.23 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 54.8833 | 89 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 100 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 974.6666 | 85 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2862 | 530 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11.7 | 27 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1126.4333 | 47 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 612.5 | 50 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.75 | 0.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3000 | 100 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 200 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3590.5 | 334 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1755.65 | 481 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 659.9999 | 360 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84.1667 | 50 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.8333 | 50 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 40.3333 | 44 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 9974.25 | 429 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 79.8 | 38 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 8.3333 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 40.8 | 6.8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 739.5 | 51 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 860-Co-generator Block
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 55595.3333 | 20 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35152.3097 | 509.7 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1202.7 | 19 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 78.5 | 15 | 1 | 1 | 1421-Secondary air fans/blowers | D2-Forced - Delayed | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1758.9 | 78 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 33.8 | 78 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 158.3333 | 20 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1184.8333 | 10 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7788 | 330 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16451.6667 | 20 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12508.295 | 17.7 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 578.8331 | 302 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5260 | 526 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 263177.04 | 788.9 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 70435.6214 | 788.9 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 774.5 | 6 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16544.2666 | 56 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 163.3332 | 140 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1051.7333 | 232 | 1 | 1 | 1430-Air supply ducts from FD fan | D2-Forced - Delayed | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 290736.6 | 126 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 113.3333 | 16 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63.2333 | 14 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3686.3333 | 20 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 252.4783 | 127.3 | 1 | 1 | 1431-Air supply dampers from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58289 | 770 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 338.4 | 141 | 1 | 1 | 1432-Air supply duct expansion joints | D2-Forced - Delayed | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5501.5999 | 206.31 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 16975 | 100 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 17.55 | 27 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1847.5 | 75 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 126 | 280 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 67726.8 | 36 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1117.0333 | 46 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 22.7998 | 342 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 110.8331 | 350 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1874.6666 | 74 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7073.2666 | 46 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3704.9997 | 855 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2410.6 | 51 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.25 | 75 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3456.1333 | 49 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15.4166 | 37 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11153.7 | 51 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 38.9332 | 292 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2.5067 | 0.64 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 882.5 | 75 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.05 | 27 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 83 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1885 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10489.2605 | 44.67 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 604 | 151 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 50 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 200 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 727.5 | 50 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 896.294 | 52.62 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20.6667 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 297.2666 | 52 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2752 | 129 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4631.1066 | 33.64 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1062 | 531 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.3333 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 440.9999 | 270 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1753 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291.6666 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 45.2 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 119.85 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12894.15 | 67 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.1666 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1952.9851 | 370.82 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 567.45 | 27 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 894.2567 | 29.24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1480 | 800 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35.75 | 55 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.55 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 96.25 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 243.4333 | 1 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3651.8 | 57 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4974.1667 | 47 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7024.5 | 27 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 18116.5 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 541.0833 | 151 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 916.3 | 539 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.6666 | 95 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 240.9166 | 245 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.6667 | 50 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282.75 | 87 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1312.856 | 60.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12450.8333 | 50 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56250 | 150 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 12691.8999 | 78 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 35 | 175 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37.5 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 117.15 | 213 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 18346.6666 | 128 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 39703.2999 | 78 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 995.3102 | 260.78 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5787.8328 | 770 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 518.6667 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 355.3333 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 306.25 | 175 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 157472.5166 | 61 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1173.8792 | 26.33 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4039.9998 | 600 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1760 | 220 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.6416 | 61.54 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1090.0803 | 23.51 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3521.4 | 18 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 34008.6667 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8.5333 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1219.8 | 57 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.58333 | 0.5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 643.3856 | 215.66 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 117.5833 | 83 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 206.1 | 18 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 47310.7167 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 300.8996 | 531 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1260.4 | 184 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 669.9 | 203 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 48.8 | 24.4 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 381.8 | 83 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 280.4999 | 153 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.9333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 147.2667 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 202.5833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4838.1666 | 182 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5208.2332 | 182 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6284.7666 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9278.15 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34112.7166 | 173 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.909 | 19.59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.6666 | 170 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.7999 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 473.7833 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 562.65 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 603.75 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 748.25 | 41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2174.9999 | 180 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3346.2 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7395.8332 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8424 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29896 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 42345.6 | 48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1207.5 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 742.3332 | 262 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84626.25 | 225.67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5281.68 | 220.07 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5293.68 | 220.57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5377.68 | 224.07 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5386.8 | 224.45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5389.2 | 224.55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 50 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 267.6665 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 472651.2 | 129.6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 699.05 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1883.465 | 23.11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 368.64 | 7.68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 4.1 | 0.41 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 40.96 | 5.12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 286.4167 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 298.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 299.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.0833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.9167 | 5 | 1 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9308.25 | 315 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 753.6665 | 190 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4267.9 | 182 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 295.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 301.9999 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 626.1 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 650 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1156.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1270.35 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1415.2 | 232 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2175.6 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3979.045 | 45.78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6090.6666 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32896.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27.45 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 142.3332 | 140 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 358.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5240.16 | 218.34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5275.68 | 219.82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5394.48 | 224.77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63615.863 | 221.89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 56.9999 | 180 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 93.4999 | 330 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 501.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 670 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6091 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 47.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 190.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 192 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 227.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 574 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3434.5665 | 187 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 9476.2499 | 171 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4803.75 | 525 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2839 | 85 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 98.7 | 42 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.0167 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.9333 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.3333 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.2333 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204.75 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 794.9332 | 271 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1615 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4225.1 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14385 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15275 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 30584.0333 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.1 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.65 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.45 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.103 | 15.21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.0333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 361.8 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 613.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 704.3667 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1326.5 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3199 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3263.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3737.5 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44280.6 | 52 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 127.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1224.9997 | 375 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1960.75 | 253 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6520 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2496.375 | 221.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5290.8 | 220.45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 26.6 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 263 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2560.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.75 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84.0833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 123.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 305.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 284.1666 | 62 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1199.7 | 558 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 88343.1 | 618 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9689.6332 | 262 | 1 | 1 | 1455-Induced draft fans | U3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.3 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.6667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 217.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 362.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 704.1832 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1581.25 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5426 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 8477.7 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12380.2666 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116.6666 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.3333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.85 | 26.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 229.95 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.55 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357.5333 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 602.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 630.1167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1759.3333 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5552.5166 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9794.25 | 135 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 510.6 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616.9167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1514.3332 | 140 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5262.72 | 219.28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5380.08 | 224.17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5398.32 | 224.93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5404.56 | 225.19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5435.52 | 226.48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24057.425 | 95.91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 16.6833 | 7.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3325.1664 | 710 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 12121.629 | 18.33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 445.8226 | 29.59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1176.48 | 8.17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2.72 | 1.36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 364 | 91 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 144.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 247 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.85 | 3 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.8333 | 10 | 2 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 57.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 186.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 288 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16250 | 125 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 8752.6665 | 190 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28734.9998 | 525 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17746.26 | 437.1 | 1 | 1 | 1455-Induced draft fans | U3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 121.6333 | 178 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.5 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 471.4667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2101.05 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2739.1 | 182 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4545.1832 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7205.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9507.3333 | 52 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 188.4533 | 19.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 202.15 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 258.05 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.7 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 346.5 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 497.2 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1842.5 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3135 | 165 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 235.6667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1622.3332 | 310 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5416.08 | 225.67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 100 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 406.9331 | 763 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 547.5 | 730 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 182.6 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 45.95 | 9.19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 164.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 224.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 433.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.9167 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 112.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43.8 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32951.25 | 87 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13307.7999 | 132 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3059.6666 | 335 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17856.6666 | 100 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2195.1 | 162 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7346.9996 | 558 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 31824.3329 | 593 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.9833 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.1833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 203.1333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.5 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.25 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 537.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19655.9 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.6 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.5333 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 264.1167 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300.3 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 319.9999 | 240 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 359.0833 | 139 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 733.0498 | 243 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1760.0333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1809 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3611.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 13768.2667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 121.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15747.3333 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2185.7625 | 221.53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5253.12 | 218.88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5276.4 | 219.85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5331.12 | 222.13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37233.6499 | 221.19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 13214.5 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 931.2945 | 23.91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1123.9763 | 19.34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 41.05 | 8.21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10744.2 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 114 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 214.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 223.5 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1765.3 | 278 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4568.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 69.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 160.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 298.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39286.5666 | 134 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 46546.5 | 465 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4922.6664 | 710 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.4 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.5667 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 249 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 279.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 322.8666 | 167 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 481.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 529.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8183.9332 | 182 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18177.25 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.7333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.7 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.7333 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.324 | 30.96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.4 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.2833 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 323.4 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 743.6666 | 115 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 746.5833 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1269.3333 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1415.8666 | 28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1441.9999 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2108.1666 | 91 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15318.3999 | 96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24402 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36453.1 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45309.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5276.88 | 219.87 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5338.8 | 222.45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5387.52 | 224.48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5400.48 | 225.02 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 13119.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 59.6 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 204.85 | 25.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 98.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 59.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 60 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 392.6693 | 24.44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 575.04 | 23.96 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 67.524 | 26.48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 322.9167 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 404.25 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.5 | 10 | 1 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 197.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 236.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 749.1666 | 145 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 309.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 199.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1068.0666 | 37 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1776.2998 | 558 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3672.5 | 565 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.75 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.5 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.1 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 179.85 | 109 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189.8 | 73 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301.1667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 459.8 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2121.6665 | 190 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10837.8666 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.6333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99 | 165 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.3625 | 13.07 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 209.5 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 211.2 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.9333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 553.3333 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1121.4666 | 104 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3120 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3726.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3748 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5280 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5862 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54672.5833 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.5 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2956.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1161.3 | 294 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1263.0533 | 220.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5197.2 | 216.55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5361.36 | 223.39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5363.76 | 223.49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5376.24 | 224.01 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5379.6 | 224.15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5385.6 | 224.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 16.6666 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 74.6665 | 280 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 7.38 | 3.69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.25 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.5 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 238.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 374.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 905 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 225.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8528 | 416 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11546.9665 | 497 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 742.105 | 63.7 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 123660 | 229 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 35169.8 | 428.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 8370 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 14041.3165 | 319 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 45 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 71.5 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13.3 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 11.25 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 30.75 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1794.6499 | 429 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 57.3 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1.8667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 12.3 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 108.9 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 165 | 30 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.1666 | 58 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7360.7666 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162.75 | 93 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 992.25 | 405 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4553.0331 | 553 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8937.5 | 650 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 207.7 | 62 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1006.4666 | 31 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2921.75 | 403 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 350 | 175 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 222 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1992.8333 | 55 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.6666 | 83 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 758.15 | 257 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.3332 | 200 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364 | 35 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1959.6499 | 231 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 940 | 200 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29121.5 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1245.8333 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13115.3666 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 310 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 651 | 325.5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6478.875 | 221.5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 484.5333 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 502.4833 | 73 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1513.6663 | 478 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 982.1333 | 232 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2751.8333 | 110 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5600 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6493.4666 | 62 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1114.75 | 35 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 37096.6666 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9486.5331 | 336.8 | 1 | 1 | 1456-Induced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.404 | 73.82 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18072.0665 | 614 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 850.5 | 270 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 233.8333 | 115 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5464.0333 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12994.2333 | 46 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 543.0166 | 31 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2164.95 | 51 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 712.8 | 19.8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 110.6 | 15.8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 370.1165 | 419 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 400 | 160 | 1 | 1 | 1456-Induced draft fan dampers | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8433.35 | 151 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 380 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1092.6665 | 220 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 305.6665 | 524 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.5998 | 254.4 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2435.4 | 198 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 514.5833 | 125 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 639.4499 | 189 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3948.3 | 73.8 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.35 | 329.4 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1185 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 828.8 | 224 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 458.2166 | 289.4 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3084.5 | 310 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.5 | 55 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 310.5 | 90 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.3999 | 224.4 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 949.5 | 90 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 900 | 108 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132.3 | 98 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 708.75 | 315 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4977.9666 | 302 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2931.2992 | 181.88 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 627.9 | 89.7 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 650-Fluidized Bed
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 59.3999 | 89.1 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 650-Fluidized Bed
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11718.6355 | 68.51 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.25 | 63 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 288.6666 | 40 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23405.83 | 51.64 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143509.8663 | 97.69 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2152.5 | 63 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11022.6666 | 140 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14141.6666 | 100 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.625 | 22.5 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5206.6666 | 80 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10333.7246 | 78.01 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12818 | 52 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13518.9 | 81 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 902 | 12 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1367.0833 | 85 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2436 | 168 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1796.43 | 46.6 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3868.9623 | 47.02 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4736.6666 | 140 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16840.0666 | 50.02 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3899 | 140 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5615.5995 | 47.61 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10728 | 240 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17832.8333 | 55 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56295.9693 | 97.64 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3938.6666 | 160 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7711.7826 | 129.32 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1082.25 | 45 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1109.9457 | 167.75 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3632.518 | 57.16 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6738.75 | 45 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7159.7667 | 30.95 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2218 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2771.6266 | 89.6 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35473.95 | 81 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2539.1666 | 55 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.496 | 124.58 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6513.7916 | 67.97 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 975.9166 | 49 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2537.8833 | 109 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10370.7 | 81 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 51.2 | 12.8 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 800-Miscellaneous
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 79.2 | 19.8 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 800-Miscellaneous
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 87.2 | 21.8 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.1666 | 230 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 714.6666 | 134 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 772 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2736 | 160 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5374.1998 | 234 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29232 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31248 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.045 | 8.34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 30.3333 | 130 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4818 | 146 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.5 | 30 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189.3333 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.217 | 14.18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 32.2 | 92 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555 | 60 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2141.5333 | 26 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6227.8331 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39255.1 | 158 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 77102.3666 | 103 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.5875 | 12.15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 251.4542 | 20.81 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1493.3332 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 165.4583 | 104.5 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 814.1333 | 142 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3858.3333 | 250 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 355.8333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 476.2665 | 304 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 686.8499 | 171 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1208 | 30 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116921.9998 | 234 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2772 | 84 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9842.7332 | 277 | 1 | 1 | 1470-Induced draft fan motors and drives | U2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 893.3332 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26093.3331 | 380 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.3833 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57848.175 | 166.95 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 15020.8333 | 156.25 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 220 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25071.1499 | 387 | 1 | 1 | 1470-Induced draft fan motors and drives | U2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 960.3332 | 215 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2858.25 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10353.7332 | 268 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 308448 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 42.5 | 85 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 894.6 | 9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2358.75 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6130.6665 | 380 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6233.0667 | 26 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28536 | 41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428.1 | 142.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1657.4998 | 450 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6756 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3.72 | 5.58 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 176 | 160 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.5 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9990 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.0666 | 296 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1030.5 | 458 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4046.8497 | 459 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28258.515 | 437.1 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200.9332 | 274 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 239.7332 | 248 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3926.6666 | 80 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 778.6666 | 160 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1022.9333 | 191.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1144.1666 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133 | 133 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 850 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 969 | 380 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 634996.2497 | 525 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1178.6663 | 544 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 82 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2419.3665 | 401 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9991.8 | 234 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30504 | 41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21.6617 | 6.34 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 159903.7333 | 238.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 988 | 380 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 718.6665 | 440 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147.5 | 118 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 383.5 | 118 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 496.3997 | 408 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 812.8665 | 274 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225.3916 | 73.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 349.65 | 113.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 844.8332 | 274 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 966.9165 | 283 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2049.75 | 27 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2456.84 | 72.26 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.65 | 5.16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 964.5996 | 546 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2714.95 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 508.7333 | 117.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 1704.0833 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 439.0833 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 235.2 | 58.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2235 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 75.4167 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 406.25 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 30 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3005.7 | 69.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 13.8 | 9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 18.4 | 12 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 1306.2165 | 181 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 191954.4 | 176 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 7177.5 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 7.5 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 477.7498 | 315 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 743.1833 | 61 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.4 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.6166 | 257 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236 | 118 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 281.0666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3360 | 320 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7875 | 125 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3317.2999 | 147 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220.8332 | 265 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.5 | 170 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 786.25 | 185 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 851.4666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 892.8 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1290.4163 | 475 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 100.7499 | 195 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 60 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 396.3333 | 116 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 603.7498 | 315 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 762.5 | 61 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 927.5 | 265 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2000 | 125 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2922.2666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3877.0666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5952 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 96.3 | 214 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 84.5833 | 175 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 649.9999 | 195 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.5332 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 993.7332 | 257 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3568.0166 | 257 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 61363.2 | 128 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.3333 | 92 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355 | 50 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 577.5 | 105 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.9332 | 233 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 360.15 | 147 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 53.3333 | 160 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1919.8 | 116 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25696.5 | 1110 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 48.95 | 89 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3649.7499 | 195 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.1332 | 257 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.8666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 438.45 | 237 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566.2666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8593.2 | 56 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 632.9166 | 245 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6190.7349 | 97.62 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16808.3333 | 100 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 208.3332 | 250 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214.9332 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 362.9166 | 335 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23575.9999 | 210 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2273.75 | 425 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D3-Forced - Postponed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.3 | 63 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1255.6416 | 169.3 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7973.262 | 402.69 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.2666 | 248 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2141.6666 | 257 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5889.333 | 560 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1350.135 | 20.55 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3842.6665 | 524 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 233187 | 285 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4197.5 | 115 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1833.3 | 21 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 800-Miscellaneous
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115 | 100 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 265.2333 | 73 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 416.5332 | 176 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 442 | 130 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18868.75 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 159.6667 | 5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2796.7998 | 228 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3779.1665 | 250 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 64.6017 | 8.3 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 112.6666 | 260 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 144.6665 | 280 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 153.9 | 342 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 10.4999 | 90 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.25 | 345 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7805 | 700 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.1667 | 19 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 465 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 554.4 | 72 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 641.7 | 138 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9874.5832 | 325 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 89167.55 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 348.8333 | 130 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 371.0667 | 8.8 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 172.6665 | 280 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 855.9998 | 321 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2327.5 | 190 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164.8333 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 96.25 | 55 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.0947 | 11.77 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7446.5 | 530 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 42.55 | 69 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55 | 60 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 602 | 60 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 52.8 | 66 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 390 | 195 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 395.8333 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 553.6999 | 147 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 633.6 | 64 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1450.44 | 142.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3343.8166 | 143 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 190 | 152 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 492.45 | 63 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 526.6666 | 200 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1306.6666 | 200 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 111.9332 | 292 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 597.6 | 12 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147920.0495 | 699 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 574.9999 | 138 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 725.22 | 142.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 998.4 | 96 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1735.9999 | 210 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 382.6999 | 258 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4083.8333 | 229 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 647.125 | 9.3 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.1833 | 11 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 82.8 | 184 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 226.5 | 302 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16217.5 | 130 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200.86 | 145.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2020.4999 | 270 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 279.2313 | 11.11 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 767.7166 | 73 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1749.9999 | 300 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 743.9165 | 395 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.9713 | 5.18 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 29.8666 | 128 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 556.9499 | 142.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 979.8 | 284 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2735.8666 | 284 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 146.7 | 54 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 253.6999 | 258 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 315 | 135 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 733.4998 | 270 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 581.6664 | 349 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 847.8167 | 13 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1837.6665 | 298 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3613.7498 | 525 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30786.6664 | 800 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 810.6665 | 380 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.4667 | 13 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 150 | 150 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.5 | 265 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 465.5833 | 151 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 137.4333 | 62 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 397.85 | 73 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1703.75 | 235 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2731.3332 | 340 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.6725 | 10.67 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 109 | 60 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1729 | 60 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2349.5 | 127 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 184.5 | 61.5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 418.6 | 59.8 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 49.3333 | 80 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 727.5 | 90 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 904.0167 | 11 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.4 | 77 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3884.3332 | 215 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480 | 160 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.6667 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6666 | 125 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 720 | 60 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3536 | 320 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31069.9997 | 780 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.6833 | 91 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1048.1667 | 38 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 321.9999 | 168 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2426.6665 | 280 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.8667 | 13 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1249.8666 | 344 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3377.9999 | 180 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5156.6666 | 170 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.75 | 147 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.1666 | 115 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 949.6665 | 220 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3138.3332 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4655 | 490 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41658.6666 | 160 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 174.1735 | 112.37 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.5333 | 22 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196.1999 | 108 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4312.5 | 250 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.75 | 33 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.4999 | 270 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5926.18 | 396.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1683.2 | 263 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1349.8333 | 91 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9732.4998 | 510 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.445 | 32.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 414.1665 | 175 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2585 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6298.1666 | 155 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 483.84 | 8.96 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15810.6664 | 770 | 1 | 1 | 1480-Other induced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1657.5 | 195 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4906.4165 | 455 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118227.3328 | 740 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.4216 | 86.53 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.75 | 45 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.5233 | 22.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.4 | 26.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.6666 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 188.6 | 92 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 880.4 | 248 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 898.3333 | 175 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10037.4998 | 330 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 768.333 | 461 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1394.8664 | 343 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24830.6666 | 110 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1057.3333 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 172 | 215 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1912.6665 | 190 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13020.8331 | 625 | 1 | 1 | 1480-Other induced draft fan problems | U2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141.8332 | 230 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1882.0664 | 436 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.14 | 26.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 369.4666 | 68 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1800 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2321.9 | 217 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2656.25 | 425 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150.15 | 33 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1275 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.0883 | 2.11 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.5067 | 1.97 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 404.95 | 89 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11349.3333 | 160 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.75 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 283.7332 | 128 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 366.9332 | 128 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1287.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.9998 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.6665 | 220 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 713.1333 | 38 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3600.6665 | 220 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 736.6331 | 287 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1713.833 | 455 | 1 | 1 | 1480-Other induced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16230.0996 | 654 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1287.4998 | 309 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 163.2666 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370.8333 | 125 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3107.5 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1950.2481 | 286.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.8333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1715.5663 | 481 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12881.1664 | 427 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1201.9 | 119 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1589.5833 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 413.6 | 176 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 477.5 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1361.6666 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.7667 | 38 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4838 | 295 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20816.6666 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69456 | 480 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1357.8 | 219 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12593.75 | 625 | 1 | 1 | 1480-Other induced draft fan problems | U3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 910 | 280 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 138.75 | 37.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 225 | 225 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 6147.9164 | 325 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 17625 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 51.48 | 12.87 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 78.8 | 3.94 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8448 | 16 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9938.3665 | 223 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1061.4 | 58 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1226.5 | 223 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9672 | 13 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3024 | 9 | 1 | 1 | 1487-Air heater (tubular) | D3-Forced - Postponed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 526 | 26.3 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 800-Miscellaneous
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.2 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.8 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.2 | 32 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.6 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.5333 | 43 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.7 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.6666 | 40 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.2 | 66 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5930.7164 | 683 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39345.8329 | 665 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11247.1666 | 179 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90632.85 | 627 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.6 | 211 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196876.4525 | 113.37 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4357.5 | 350 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 113.7499 | 195 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 372.0833 | 235 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.5833 | 25 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158840.8 | 844 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109481.1664 | 770 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.0333 | 82 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.6666 | 185 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11509 | 30 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 416 | 260 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3982.1332 | 436 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.75 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.4 | 24 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.2333 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.1666 | 31 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.5333 | 16 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.4167 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.4 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 95.4 | 27 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7131.9166 | 115 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1347.0831 | 305 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9995.6666 | 314 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 495.2666 | 46 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15010.2 | 279 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.8 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.2 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.8 | 9 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.0167 | 23 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.3333 | 28 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.7333 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.0333 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.3333 | 40 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.5333 | 16 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 41914.1328 | 824 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7312.9999 | 213 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26762.4 | 531 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46336.8331 | 410 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.9333 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.35 | 9 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.7833 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.7 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.6667 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.4 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.65 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.1333 | 38 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.5833 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.6667 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.7 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.6 | 24 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.0333 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2563.2081 | 677.5 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5309.7499 | 201 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2511 | 620 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1266337.3329 | 665 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54 | 4 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2645.3331 | 320 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3562 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4379.2 | 644 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36450 | 375 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 360.3333 | 235 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.6 | 36 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.8667 | 23 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.3333 | 10 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.6333 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.55 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.25 | 45 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20279.8331 | 677.5 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119317.3329 | 680 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6200.0833 | 235 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.8332 | 146 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1470 | 350 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2024.7666 | 278 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7270.9999 | 330 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15364 | 120 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3488 | 436 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 30.75 | 9 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.8667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.4667 | 11 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.0833 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.95 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42.75 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6763.9665 | 262 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19524.9166 | 335 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12720.3998 | 231 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5774.8411 | 419.48 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170.8333 | 205 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.2833 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.3 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.95 | 23 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.3167 | 29 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.5 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 26.9167 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.7333 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 7411.4533 | 497.97 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4521.15 | 334.9 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 299.2665 | 268 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 650-Fluidized Bed
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2980.9999 | 330 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 848.6665 | 190 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6525 | 90 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.3332 | 310 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 616 | 110 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 28.9333 | 56 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 26.25 | 175 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2729.9997 | 504 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 155961.8664 | 728 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 64176 | 21 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.2 | 6 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 808.84 | 5.54 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3901.8 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4293.5 | 31 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 889.8 | 18 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1155 | 11 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1452.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27435 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2304.5 | 11 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 120 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20000 | 125 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1434 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2405.2 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2592 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3184.8 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16077.0399 | 79.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 633 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4760 | 32 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 486.6666 | 200 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 612 | 68 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.4 | 9 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2058.53 | 10.2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.6016 | 34.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28201.39 | 106.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24907.1853 | 93.73 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.1 | 63.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.75 | 27 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236 | 16 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1410 | 36 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 58.74 | 5.34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 67.15 | 3.95 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 116.9703 | 4.18 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 257.04 | 15.12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 3 | 3 | 1 | 6 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 4.66 | 2.33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 4.7402 | 2.39 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 18 | 3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 654.16 | 6.29 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6373.9667 | 41.3 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 145.3333 | 20 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1082.9167 | 23 | 1 | 1 | 1500-Air heater soot blowers | U1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5250.5 | 10 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.5333 | 8 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 878.2167 | 23 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 608.3999 | 351 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 685.0667 | 14 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2372.5832 | 355 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.6333 | 11 | 1 | 1 | 1512-Flue gas expansion joints | D2-Forced - Delayed | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72743.9996 | 630 | 1 | 1 | 1512-Flue gas expansion joints | U3-Forced - Postponed | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8575.9525 | 31.97 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115676.25 | 849 | 1 | 1 | 1512-Flue gas expansion joints | SF-Startup Failure | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18691.5 | 510 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23499 | 315 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2082.5 | 15 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2085 | 15 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 341.6 | 16 | 1 | 1 | 1512-Flue gas expansion joints | D2-Forced - Delayed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14174.8 | 24 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 802.75 | 57 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D2-Forced - Delayed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1088.9999 | 270 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3638.6667 | 20 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 133.3999 | 138 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42087.7997 | 762 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U2-Forced - Delayed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.0833 | 5 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2538.6666 | 64 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.9167 | 11 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15879 | 10 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 40 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 251.25 | 25 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1128 | 12 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3669.7912 | 677.5 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 54708.333 | 500 | 1 | 1 | 1530-Other flue gas problems | U2-Forced - Delayed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 545.4 | 404 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.1 | 14 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.2575 | 25.05 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65.3333 | 70 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2088.3331 | 350 | 1 | 1 | 1530-Other flue gas problems | D3-Forced - Postponed | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 20350 | 407 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11387.3331 | 380 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 138902.6665 | 380 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 432.9332 | 382 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19595.5666 | 137 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10786.3998 | 291 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4314.7996 | 552 | 1 | 1 | 1535-Flue gas recirculating fan | U1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2142.4349 | 209.7 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8017.4997 | 450 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1536 | Flue gas recirculating fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4518.5164 | 361 | 1 | 1 | 1536-Flue gas recirculating fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2152.8 | 138 | 1 | 1 | 1550-Flue gas recirculation fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1560 | Other flue gas recirculation fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 75.1216 | 95.9 | 1 | 1 | 1560-Other flue gas recirculation fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2182.4833 | 91 | 1 | 1 | 1570-Flue gas recirculation ducts | D1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9162.4995 | 750 | 1 | 1 | 1570-Flue gas recirculation ducts | U1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3284.2333 | 106 | 1 | 1 | 1570-Flue gas recirculation ducts | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2180.9666 | 91 | 1 | 5 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2182.4833 | 91 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1102.6166 | 91 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 949.4333 | 91 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 37880.2666 | 91 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2631.4165 | 455 | 1 | 1 | 1580-Flue gas recirculation dampers | SF-Startup Failure | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2438.55 | 27 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 922.05 | 81 | 1 | 1 | 1580-Flue gas recirculation dampers | D2-Forced - Delayed | 100-Fossil-Steam
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 169.6249 | 172.5 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 505.9999 | 330 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131.8333 | 113 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 62.5 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1253.7 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.45 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61 | 61 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.92 | 3.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.94 | 4.26 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 565.36 | 7.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1726.6666 | 70 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.1 | 4.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1357.4165 | 455 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4892.25 | 593 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5831.4664 | 448 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13050 | 435 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 115.2797 | 432.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.96 | 13.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 237.17 | 6.41 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305.8333 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 693.16 | 11.18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1949.222 | 18.04 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.09 | 2.83 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1015 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1316.7 | 6.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5300 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.2228 | 9.83 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23.4666 | 64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3906 | 434 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45981.8328 | 770 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U3-Forced - Postponed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92 | 46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 241.92 | 11.52 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.86 | 4.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.98 | 4.57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.09 | 3.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 658 | 9.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720.9 | 8.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5190 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 944 | 236 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1952.65 | 147 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 198.99 | 6.03 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 570 | 57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 646.3 | 5.62 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.02 | 3.93 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.95 | 3.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 369.8 | 8.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420.98 | 13.58 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1097.25 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1254.3 | 11.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12247.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.95 | 1.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124.08 | 5.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440.3333 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 576.83 | 15.59 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 328.6666 | 290 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 102.3 | 93 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25177.8 | 29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 265.25 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4163.6 | 24 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 43200 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128 | 8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.84 | 4.83 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 308.7 | 4.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1165.6 | 6.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4693.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61 | 1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 206.25 | 165 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5511.9167 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 46.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 105.0833 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 51840 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 21.5 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 366 | 30.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 511.7 | 5.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345.32 | 3.88 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 600 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1429.1666 | 70 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3004.5817 | 10.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 270.81 | 5.31 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1701.333 | 440 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 498.8331 | 730 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 316.6665 | 190 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9584.5 | 29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.9 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 65.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1308.3395 | 58.89 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1480.3 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.92 | 3.52 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.9 | 4.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.6 | 7.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.96 | 11.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.96 | 8.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454.06 | 6.22 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.7 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.94 | 6.21 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.97 | 1.77 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.8 | 1.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 149.8333 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 292.4 | 4.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.95 | 10.45 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 492.8 | 30.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6720 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21900 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.86 | 6.34 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325 | 25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5560.7499 | 435 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2595 | 51.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29409.3833 | 29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3369.4666 | 37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.12 | 1.09 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 4.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.96 | 6.07 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.8 | 1.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.8667 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2121.84 | 336.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | SF-Startup Failure | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 937.6666 | 290 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12030.4665 | 181 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 886.5997 | 429 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1198.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 55 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 33.3333 | 25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 287666.851 | 137.38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 18.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | WECC | Winter | 11.7 | 27 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 860-Co-generator Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266 | 66.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348 | 232 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 392.5 | 157 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 130 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3004.1666 | 103 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 46.6665 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 582.9998 | 330 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 651.75 | 395 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1485 | 900 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2590.8 | 127 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2459.3331 | 595 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 15 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 235.2 | 294 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 591 | 295.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 128.2833 | 43 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 180.9333 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 627 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1786.6662 | 670 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.7095 | 74.91 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2370.5 | 110 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 339.84 | 566.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 623.04 | 566.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 481.4665 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.6165 | 199 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 762 | 254 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2704 | 338 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 493.6533 | 231.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1431 | 95.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 276 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2364.9998 | 330 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4930 | 850 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6982.7499 | 255 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 77.1813 | 16.48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 481.44 | 566.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 150.3332 | 164 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 589.05 | 153 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.8333 | 130 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 571.65 | 103 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 137.4998 | 330 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2115.1664 | 370 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2479.95 | 99 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 299.6484 | 382.53 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 180.8333 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 980.8333 | 110 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7260.1666 | 98 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 420 | 56 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 123.3332 | 370 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2269.3332 | 370 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 570.3331 | 290 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2426.6913 | 575.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.0666 | 329 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 520 | 130 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 978.3666 | 98 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2470 | 130 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3094 | 102 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 147.6332 | 206 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 226.1998 | 261 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1893.1664 | 370 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1386 | 330 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.6665 | 220 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1344 | 448 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 608 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.0998 | 501 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 714 | 204 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1920.96 | 83.52 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 367.3666 | 103 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 71.1666 | 122 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 294.6666 | 260 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.8333 | 46 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 522.75 | 255 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2408.8331 | 745 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 707.4 | 524 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3525 | 564 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 483.6 | 117 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3835.4166 | 125 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 542.0666 | 173 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 18.3333 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 256.8331 | 335 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 549.7332 | 532 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.5 | 270 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 967.4999 | 270 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1124 | 281 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 198.5166 | 43 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 5674.1998 | 252 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 2155.8293 | 499.42 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 2146.23 | 427.82 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 4510.5199 | 434.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 2460 | 400 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 831.1615 | 234.13 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 1156.8161 | 137.99 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 6453.2037 | 428.31 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 2933.8105 | 447.91 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 321.9967 | 272.11 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 2996.2165 | 277 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 372.6449 | 132.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 894.6665 | 488 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1189.8998 | 489 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 50.1666 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2857.6333 | 103.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 240.5333 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2252.5012 | 544.96 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 158.9333 | 59.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 190.722 | 272.46 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 776.0925 | 270.73 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 963.93 | 29.21 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 474.9333 | 208 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 845.8665 | 488 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1066.3332 | 457 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 353.0733 | 21.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 144.9583 | 173.95 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 285.9999 | 195 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 7.4667 | 14 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 489.9999 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 757.1666 | 192.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 263.9 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 445.9 | 147 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1818 | 180 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 823.15 | 163 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 65.3333 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3459.1333 | 178 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 70.7183 | 28.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 1318.8666 | 146 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 6146.9333 | 178 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 84.7332 | 164 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 760 | 152 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 259.1333 | 169 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2470.5166 | 227 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3892.028 | 222.19 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 53.625 | 49.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 120.75 | 161 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 226.1728 | 64.93 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 912.3332 | 230 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 650.5833 | 211 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 22265.1 | 173 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 517.6499 | 153 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 18.6667 | 35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 142.2 | 237 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 131.95 | 91 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 23.9999 | 90 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 783.0333 | 139 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Summer | 242.6666 | 80 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 371.3 | 141 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 763.9999 | 120 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 401.7999 | 123 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 619.8498 | 483 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 539.4665 | 238 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1291.4999 | 135 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 250.75 | 51 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 13 | 12 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2129.9499 | 123 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 150.42 | 49.05 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 122.6332 | 283 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 168.6666 | 110 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3678.4999 | 210 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | SERC | Summer | 61.6666 | 100 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 861-CoG GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | SERC | Winter | 34.65 | 33 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 861-CoG GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 94.25 | 65 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 862-CoG steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 800.4 | 12 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 28.4999 | 342 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 903.8333 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.3333 | 175 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12976.5996 | 546 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 376.25 | 215 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 464.3333 | 70 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 222.4167 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 121.5 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D3-Forced - Postponed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2147.5 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D3-Forced - Postponed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 885 | 590 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 240 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1142.8165 | 359 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.6666 | 65 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217 | 310 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 66 | 55 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 107.0665 | 292 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 403.8667 | 8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D3-Forced - Postponed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 330.3998 | 566.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 195 | 195 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 270.6665 | 280 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.5333 | 77 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 423.4666 | 64 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.3333 | 20 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1330.3 | 502 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.9999 | 375 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28616.5333 | 38 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 153.75 | 205 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 202.1332 | 379 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 243.1 | 13 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 331.2 | 184 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 731.4998 | 570 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 987.9998 | 240 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13329.9996 | 600 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 236.5 | 110 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 906.2497 | 375 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 690.75 | 45 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 161.25 | 43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1524 | 762 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 116.0333 | 118 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 5190.1 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 480 | 60 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.85 | 37 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1413.2663 | 493 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3894.8 | 28 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11245 | 1300 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 478.4 | 299 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 26.4 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.1 | 3.1 | 2 | 4 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.2 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 1938.6831 | 293 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3 | 3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.2 | 3.2 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.7 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.1 | 3.1 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.8 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 35.2 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.9 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 136.2 | 18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.1 | 3.1 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.8 | 3.4 | 1 | 4 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7.2 | 3.6 | 1 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.3 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.8 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13.2 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 35 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.6 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 9.9 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 22.4 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 28 | 5.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10.8 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 28 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.4 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.2 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.4 | 3.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7.6 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7.8 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.8 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 23.8 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34.2 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.4 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.2 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.3 | 3.3 | 2 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.6 | 3.3 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.8 | 3.8 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14.8 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10.2 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 20.4 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 832.5 | 185 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 1119.25 | 185 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 7.4666 | 28 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 6.0666 | 28 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.3332 | 200 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21464.3 | 39 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11988.9998 | 285 | 1 | 1 | 1720-Desuperheater/attemperator controls | U2-Forced - Delayed | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 103.3332 | 248 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 278.8665 | 356 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1267.2163 | 547 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5061.1331 | 356 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 783.9582 | 376.3 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2211.65 | 497 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1259.0497 | 447 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 458.4999 | 105 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 9.3333 | 112 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4950.4 | 448 | 1 | 1 | 1720-Desuperheater/attemperator controls | U2-Forced - Delayed | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4879 | 697 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2050 | 41 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4311.6664 | 650 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1746.9 | 647 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4194.3499 | 447 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4115 | 30 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3149.9995 | 675 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 456.3998 | 489 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 882.0165 | 283 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 13706.604 | 276.25 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 329.9166 | 185 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 427.8333 | 151 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 643.7 | 157 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 36.8332 | 221 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 214.6666 | 230 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 56 | 70 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 109.7633 | 25.33 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 88.1386 | 165.26 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 209.95 | 221 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 2709 | 215 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 221.9999 | 180 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 898.45 | 151 | 1 | 1 | 1720-Desuperheater/attemperator controls | U2-Forced - Delayed | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 104 | 130 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 480.9583 | 242.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 171 | 180 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 582 | 194 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 312.9665 | 229 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 170.7617 | 35.33 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 184.1666 | 221 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 495.8333 | 250 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 187.25 | 105 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 58.5 | 130 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 200.5332 | 128 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 616.3999 | 138 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 99.75 | 105 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 188.5 | 130 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 63.3333 | 190 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 516.1665 | 190 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 95.2 | 119 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 129.5 | 105 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 192 | 256 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1730 | Boiler explosion or implosion | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.4998 | 249 | 1 | 1 | 1730-Boiler explosion or implosion | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 849.1949 | 305.1 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 244.1667 | 50 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 897.4485 | 206.31 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1106.9999 | 405 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 45.5999 | 342 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 91.2499 | 75 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 19 | 60 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.7 | 339 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1468.5 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 282.75 | 435 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 323.4333 | 62 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.75 | 25 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1020 | 75 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1079.1499 | 339 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 653.95 | 451 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 443 | 443 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 8402.0333 | 62 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 545 | 75 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 660 | 75 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 70.76 | 8.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 126.3332 | 379 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1056.3999 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3005.3332 | 230 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 28.9997 | 435 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 127.5 | 50 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 21.6667 | 26 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8134.5664 | 881 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 589.8666 | 158 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1801.333 | 560 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 122 | 244 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 130.935 | 124.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 154.5333 | 38 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1282.1283 | 82.1 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 186.6665 | 280 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3190.05 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 971.7 | 158 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10.8333 | 50 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 430.21 | 430.21 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4483.4166 | 335 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252.8 | 96 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 661.4664 | 451 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1566.2749 | 437.1 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 689.75 | 445 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1072.8328 | 785 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4919.3328 | 785 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 16.7833 | 19 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3272.1666 | 290 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 329.1665 | 395 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 396.3331 | 290 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 3244.2663 | 553 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3011.25 | 73 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 231.5248 | 283.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 41.65 | 51 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U3-Forced - Postponed | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 712.3999 | 312 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 148.2831 | 287 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 212.9999 | 180 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 743.6 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 5815.1666 | 230 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 232.1416 | 156.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 3294.4504 | 225.39 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 99.8999 | 162 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 609.1666 | 170 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U2-Forced - Delayed | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 312.9833 | 211 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 746.4166 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1078.7833 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 4509.4833 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 63.9 | 142 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 7433.6 | 202 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 20.3333 | 152.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 3069.4999 | 210 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Winter | 2988.5333 | 112 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 157.9333 | 51.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 797.1165 | 283 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 116.4 | 72 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1621.3331 | 320 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5.3333 | 20 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 3034 | 120 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 1245.4166 | 152.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 680.8333 | 190 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D2-Forced - Delayed | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | NPCC | Winter | 85.6 | 24 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | SERC | Winter | 143.65 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 416.8666 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 11.9 | 21 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 862 | CoG steam units | SERC | Off-Peak | 328.0666 | 133 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 862-CoG steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 862 | CoG steam units | SERC | Winter | 113.05 | 133 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 862-CoG steam units
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 258.3332 | 310 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 609 | 348 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 165.2 | 28 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 828.6665 | 440 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2239.72 | 336.8 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 645.8832 | 271 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2435.15 | 431 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1070.3876 | 605.88 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.8713 | 72.53 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 136.8 | 342 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 148.1999 | 342 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 187.85 | 289 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 298.8331 | 326 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 146783.5831 | 721 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1210.95 | 351 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 195.4831 | 317 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 28.05 | 187 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 341.1666 | 230 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 146.6666 | 88 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1178.9923 | 477.97 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1523.9666 | 131 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5078.4332 | 262 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 580.6666 | 130 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5114.1664 | 361 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1012.5388 | 497.97 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4010.0662 | 661 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 85960 | 560 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 92.4665 | 292 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 141.3332 | 212 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1853 | 15 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2633.5833 | 187 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2802.4664 | 662 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3180.3331 | 290 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6836.6331 | 634 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 254.1916 | 64.9 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 759.6665 | 530 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2492 | 712 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 335.6665 | 380 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2710.9197 | 495.9 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14.1833 | 23 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 504.8333 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.385 | 120.66 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 47.9166 | 125 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 831.85 | 131 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.4431 | 306.2 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.9781 | 307.7 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4770 | 75 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 478.7333 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.9498 | 249 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 293.8573 | 144.52 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 116.8 | 292 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 350.6333 | 157 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 735.4666 | 28 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 301.6 | 208 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 694.1666 | 175 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1560 | 208 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1962.6666 | 230 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3599.8463 | 548.2 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19708.3331 | 625 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 563.2 | 352 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 798.8166 | 167 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 211.2 | 528 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 90.5666 | 104.5 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 391.9998 | 336 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 884.7997 | 474 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227.1018 | 164.17 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 271.6164 | 379 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.697 | 106.33 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 163.3332 | 280 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 85 | 34 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 266.7998 | 348 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 461.7 | 162 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 541.4666 | 131 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1235.6166 | 89 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280.3331 | 580 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1695.4664 | 352 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2842.6663 | 520 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8597.6032 | 548.2 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1243.1997 | 504 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1760.9163 | 565 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.9 | 114 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 858.1665 | 190 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1183.7 | 623 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 18.95 | 379 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1395.1333 | 68 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1442 | 280 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 70.6333 | 13 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 207.1666 | 113 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 326.4 | 326.4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 495.7333 | 88 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 772.8 | 386.4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2506.4666 | 164 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 249.6666 | 140 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1166 | 530 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2099.3098 | 495.9 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4243.3331 | 380 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 141.9 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 259.96 | 53.6 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 737.1 | 351 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 390 | 150 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 234.5 | 67 | 1 | 2 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 776.0833 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 114.1 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1.4 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 24.8 | 48 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 132.5 | 30 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 541.75 | 197 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 31.6667 | 20 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 74.9833 | 11 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 113.05 | 19 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 234 | 26 | 1 | 2 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 372 | 31 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 84 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 198.1 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2.4 | 24 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 58.7666 | 86 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 152.25 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 4.6 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 37.6166 | 37 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 125.3 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 155.1 | 18 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 256.5333 | 26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2709.35 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 243.2 | 48 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 12.4 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 48.6666 | 40 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 99.75 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 56 | 60 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 402 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 720.9165 | 211 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3.0667 | 23 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 75.9333 | 68 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 228.9166 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 33 | 60 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 159.25 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 8 | 24 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3 | 1 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 210.8667 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.0667 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 108 | 90 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7.4666 | 28 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 102.5 | 30 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4885.3333 | 80 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 14.7 | 63 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 52 | 8 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 31440 | 80 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 48.4 | 44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 135.96 | 10.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1317.9166 | 25 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 448.2 | 99.6 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 596.0965 | 110.73 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 81 | 27 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 26520 | 80 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 1145.6666 | 28 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 862-CoG steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.0332 | 134 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 736.2663 | 502 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 16.1 | 42 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 433.7483 | 64.9 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 56.7133 | 18.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 800-Miscellaneous
1760 | Feedwater instrumentation (not local controls) | NULL | NULL | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 124.8 | 20.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 800-Miscellaneous
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 708.3998 | 231 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6 | 6 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 252.8332 | 185 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 245.7332 | 152 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 703.7916 | 47.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U3-Forced - Postponed | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 198.6666 | 149 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 480.9583 | 242.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 332.5832 | 307 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 227.0333 | 139 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 197.9499 | 160.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 28 | 28 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 443.3 | 26 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 170.8332 | 125 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Summer | 48.3331 | 290 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 1688.1 | 102 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 861-CoG GT units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 877.15 | 53 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 862-CoG steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630 | 35 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1840.1328 | 746 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.6666 | 95 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 253.3333 | 160 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 107.6664 | 340 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9902.1665 | 590 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10468.8 | 654.3 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 191.6666 | 230 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 284.1998 | 348 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1058.6332 | 349 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 191.4 | 99 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2924.8 | 457 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 48 | 20 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 70954 | 13 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660 | 400 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3616.2 | 196 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1146.8 | 47 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253.2997 | 447 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1241.6832 | 367 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1976.3665 | 422 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 709.05 | 489 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 290.9999 | 180 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 159.8833 | 181 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 549.0333 | 181 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3329.3 | 169 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 169.7499 | 105 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.6666 | 160 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1999.75 | 421 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1945.9999 | 210 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1863.833 | 530 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4658.3171 | 662.32 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11568.5222 | 662.32 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2199.1665 | 650 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 15452.1499 | 147 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 101255.1998 | 552 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 16.6478 | 16.93 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204 | 240 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 586.925 | 138.1 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1385.9076 | 372.89 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3080.9996 | 585 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2356.6665 | 280 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 352.8 | 36 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 270 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 550.25 | 155 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 990 | 5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 354.8913 | 575.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 586.95 | 43 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 659.75 | 39 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 25567.8 | 258 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2512.5 | 750 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2034.9 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1062.2164 | 391 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 327.4999 | 393 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12699.9998 | 750 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 23.115 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 314.3358 | 496.32 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 590.8 | 6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 183.7333 | 106 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17.4 | 58 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1321.1332 | 149 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1579.5 | 162 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D3-Forced - Postponed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.4833 | 37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 788.8 | 493 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12230.8422 | 662.32 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1369.5499 | 147 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 95.2 | 136 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 266.4166 | 139 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 657.3333 | 136 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6474.9997 | 750 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 16.5825 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 581.295 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 133.34 | 133.34 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 717.8333 | 118 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.5 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1505 | 21 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 407.9167 | 25 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.411 | 153.59 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 291 | 18 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4824 | 36 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 25 | 100 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 9681.6664 | 785 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.25 | 37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 901.9831 | 299 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 922.8332 | 245 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 567.1664 | 415 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 45.7333 | 56 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 17925 | 750 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 246.4 | 448 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 262.4883 | 105.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 444.015 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4225 | 650 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 671 | 110 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 220 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1300 | 208 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2029.2 | 712 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2085.0831 | 655 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 58576.05 | 741 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 4089.8 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.0333 | 118 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141 | 470 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.0667 | 4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.25 | 3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.75 | 21 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 589 | 380 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1549.1663 | 550 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.3331 | 410 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 396 | 528 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 76.505 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 802.23 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1650.25 | 287 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 959.5 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1764.9999 | 300 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7105 | 700 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 15 | 18 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 900 | 225 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 191.7 | 63.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 653.83 | 129.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 56.9643 | 23.41 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.6833 | 37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 43 | 86 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1134.3332 | 415 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 9.258 | 46.29 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 600.6 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2020 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 12 | 12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 14918.9999 | 180 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | WECC | Winter | 602.6453 | 33.92 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 35.3966 | 25.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 70 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 65.8667 | 19 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 179.1 | 398 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 575.0667 | 19 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 419.833 | 458 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 214.6665 | 368 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 772.6665 | 488 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 43 | 86 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2013.0199 | 150.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 24.9333 | 34 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 346.8665 | 236.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 64.5166 | 49 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 45.7519 | 98.04 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 1.1 | 33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 35.2 | 48 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 16.5 | 33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 50.9166 | 65 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 43.2833 | 49 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Summer | 22.876 | 98.04 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 868.25 | 377.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1062.105 | 172.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 10105.3328 | 848 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1103.45 | 761 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 403.5979 | 98.04 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 550.6579 | 98.04 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 15.08 | 37.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 28.945 | 82.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 228.6165 | 236.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 36.0333 | 46 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 838.3166 | 179 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 100.6999 | 159 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 235.5 | 157 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 211 | 211 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 448.2928 | 226.03 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 726.7 | 338 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 40.2333 | 142 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 44.9666 | 142 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 215.3332 | 170 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 85.631 | 122.33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 26.08 | 48.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 240.6999 | 174 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 573.2165 | 211 | 2 | 2 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 92.1666 | 158 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 143.1 | 159 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 572 | 176 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 213.9166 | 151 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 23.1 | 49.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 171.0999 | 174 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 178 | 178 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 1029.3333 | 160 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 768.8165 | 283 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 1702 | 74 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 6 | 12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 135.6 | 226 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 141 | 141 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 213.2 | 123 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2405.6 | 248 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 566.6833 | 121 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 120.95 | 123 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 170.15 | 123 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 127.2705 | 19.53 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 155.7999 | 123 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 57.3997 | 492 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 61.6 | 105.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 253.7499 | 105 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 374.4999 | 210 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 430 | 200 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2244.6666 | 104 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 55.2099 | 165.63 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 197.946 | 282.78 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 112.6249 | 79.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 8 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 82 | 410 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 4105.5 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1796.05 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1037 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 621 | 23 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 858.5 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 4373.25 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2328.7167 | 17 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3456.4833 | 13 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 462 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11552.0166 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1347.3333 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 3997.7833 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 8480.1 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1210.95 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 4432.8667 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 660 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 962 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1662.93 | 24.3 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1731.25 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 8 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7699.0833 | 55 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 0 | 0 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 599.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1815 | 55 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2253.3333 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3569.15 | 51 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 650 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1558.9166 | 65 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 744 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 930 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1505.79 | 24.3 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3032.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1134 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1440 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 648 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 713 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 48580 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 595.4167 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 778.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 825 | 33 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 874.4167 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 990 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 840 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2071.8333 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 675 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 713 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 705.8333 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1239.5833 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1938.75 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2321.25 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 670.1166 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 51.3 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 348.2966 | 25.3 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 815 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 980 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 435.6 | 22 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 525.9666 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 945 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 4418.75 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 651 | 31 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2468.75 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 57.5 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.2165 | 193 | 1 | 1 | 1810-Other boiler inspections | U1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2446.5 | 30 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 800-Miscellaneous
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3045.5 | 30 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 800-Miscellaneous
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.395 | 10.05 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4369.9999 | 285 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 80 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D2-Forced - Delayed | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18571 | 196 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 233.75 | 75 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1260 | 315 | 1 | 2 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14788.5583 | 70.9 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413328 | 632 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 571.2 | 17 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 3814.8 | 17 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1236.1833 | 17 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 3589.65 | 26.59 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1072.9833 | 17 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21212.565 | 64.9 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 433.2167 | 17 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 337.365 | 24.3 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 650-Fluidized Bed
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 12188.2333 | 106 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 850-Combined Cycle Block
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6044.5666 | 58 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U3-Forced - Postponed | 851-CC GT units
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 336.0666 | 71 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 851-CC GT units
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 209.7666 | 58 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U3-Forced - Postponed | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 159.6 | 228 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.2 | 54 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 180.8333 | 175 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.6666 | 128 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 490.2673 | 149.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 663 | 68 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2601 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2613.5199 | 172.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4802.2675 | 176.23 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5741.0499 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.6833 | 41 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 332.5 | 266 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3199.5 | 474 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1170 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1577 | 166 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3773.105 | 160.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 329.15 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 124.4833 | 97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5437.2 | 197 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 392.9165 | 205 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 493.0499 | 171 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 165.1833 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 406.9999 | 165 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2105.8333 | 70 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11188.3333 | 175 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 221.95 | 69 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 519.75 | 33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1539.7 | 173 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2827.5 | 145 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2041.2333 | 38 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.3332 | 140 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.6666 | 230 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 623.1833 | 139 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680.1666 | 77 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 906.7833 | 41 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4372.3999 | 204 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 398.1999 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 988.25 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 206.5832 | 185 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1370.7666 | 118 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220.5 | 105 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3289.9 | 167 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 86.3333 | 70 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 235.75 | 23 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400 | 20 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 720.7833 | 59 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 967.5999 | 123 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1608 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15743.1665 | 295 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91.2 | 96 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196.5 | 131 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2116.8833 | 157 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 154.5333 | 61 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 214.6666 | 230 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1886.3832 | 259 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2856 | 238 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 379.2332 | 367 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 162.3999 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 252.3 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 343.2 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 939.5832 | 275 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 54.1333 | 29 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 22.6666 | 80 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 68300.75 | 217 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.4332 | 266 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 24924 | 90 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 115519.3667 | 38 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.5 | 79 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 134.32 | 134.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 180.88 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 682 | 22 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1377 | 162 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5475.7799 | 313.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21439.1031 | 306.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1100 | 200 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1237.6333 | 107 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3056.9333 | 101 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 147.4666 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 149.3333 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 292.5999 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 496.5999 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10568.8833 | 79 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 29.2499 | 135 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 178.6666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3180.2832 | 209 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 930 | 93 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1249.8949 | 137.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2898 | 161 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1246.9999 | 174 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 126.6666 | 95 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 605.2 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6567.42 | 475.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 93.5 | 170 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7752.6666 | 290 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 390.1166 | 89 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1022.25 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1306.0833 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2055.8166 | 173 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4349.4859 | 115.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.7 | 81 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.6331 | 326 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 199.7499 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 468.93 | 89.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 552.6359 | 139.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 837 | 93 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 74.6667 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 175.5 | 45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3021.965 | 475.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 170.85 | 201 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3964.2999 | 174 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.15 | 43 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58.75 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.8 | 78 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79.5832 | 191 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 269.9666 | 91 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 286.3666 | 71 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 402.0499 | 129 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 423.2999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2348.599 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3324 | 277 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1341.8333 | 166 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3067.1999 | 162 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 265.8333 | 145 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 337.85 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 391.5 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 512.0498 | 231 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 139.3999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 8.75 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 45 | 135 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 283.3333 | 50 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.5 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5980.8 | 712 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4554.6664 | 427 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280.98 | 187.32 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 801.6 | 72 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2630.3675 | 52.45 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3920.6166 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5 | 1.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 367.2 | 216 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1254 | 57 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4813.6833 | 169 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9683.3332 | 125 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.6666 | 34 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 701.7332 | 277 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 724.8165 | 277 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1559.6333 | 142 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 310.2332 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 737.75 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 100.215 | 45.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6192.5816 | 245.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 481.3333 | 190 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2069.3333 | 97 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 7528 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1409.2999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 6235.65 | 279 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2021 | 86 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2417.6833 | 119 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 178.9867 | 12.8 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 229.6 | 32.8 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 175.0653 | 283.89 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 189.97 | 172.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 73.08 | 182.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 95.79 | 92.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 295.12 | 95.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2283.5933 | 121.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3156.305 | 120.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 296.98 | 95.8 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 1644.8 | 257 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 192.1 | 113 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 2689.0465 | 321.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 0 | 0 | 1 | 3 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 449.96 | 321.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1900 | Improper balance between tube sections not due to fouling or plugging | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 682.9166 | 275 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | D1-Forced - Immediate | 100-Fossil-Steam
1900 | Improper balance between tube sections not due to fouling or plugging | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 211 | 12 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | D1-Forced - Immediate | 800-Miscellaneous
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 0.83333 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 110 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D3-Forced - Postponed | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42000 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4233 | 1 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9.1667 | 50 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 16.9 | 3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.1167 | 7 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.2167 | 13 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 350 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4194 | 1 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4418 | 2 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 123.9333 | 13 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12798 | 3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214.5 | 8.58 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 231.7666 | 34 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11.8333 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 47 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 149.5833 | 25 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 274.3 | 6 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 7443.3333 | 110 | 1 | 1 | 1910-Inadequate air not due to equipment problems | U1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1624 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.3 | 23 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 141430.8333 | 94 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5.6667 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 52.5 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 66.8333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 102.5 | 20.5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.15 | 9 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 85 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23040 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4355.07 | 8.11 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 49.8667 | 8 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 96.6667 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 31.3333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.5 | 50 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 30 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 74 | 74 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.3333 | 50 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 908.3 | 293 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 240.75 | 321 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.6499 | 171 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1497.45 | 149 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1617.75 | 135 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3763.3832 | 349 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 697.74 | 116.29 | 2 | 2 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 70.3999 | 192 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1835.8 | 137 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2975.4 | 261 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1458.4165 | 407 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1487.4 | 402 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.25 | 27 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1070.9998 | 270 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 806.6666 | 121 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1021.7499 | 201 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 779 | 380 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1380.683 | 443 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 21.5 | 30 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1733.3333 | 160 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.3333 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 624.6333 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 12 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1016.5 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 306 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 321.875 | 10.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 143.075 | 9.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1036 | 280 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 8475.6333 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 15.5 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 44.0833 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.01 | 4.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4 | 3.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 1 | 6 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.03 | 2.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19 | 3.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.1 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.05 | 1.65 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.96 | 2.14 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.6 | 2.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.99 | 12.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.97 | 1.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.8 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 7.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4416.9331 | 628 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 27439.2 | 824 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 462.3331 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 144 | 240 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3509.5166 | 43 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3074.1667 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9827.2997 | 417 | 1 | 1 | 1999-Boiler; miscellaneous | U3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.9999 | 330 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 52.3167 | 8.6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 714 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 38.3333 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 102.6666 | 28 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.9 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 7 | 14 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.01 | 2.67 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 5.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.95 | 2.15 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 4 | 6 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.8 | 2.7 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.98 | 2.18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2288.8 | 48 | 2 | 2 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3333 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1447.6 | 658 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19572.7847 | 382.53 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 64477 | 427 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 95601.9163 | 517 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5633.3499 | 183 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 164300.5329 | 593 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.3332 | 460 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375.8331 | 410 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3820.0631 | 617.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 483.9856 | 33.34 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 5142.5833 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 35.2 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 164.3332 | 170 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 15039.7166 | 103 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.01 | 8.67 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.01 | 9.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17 | 3.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.04 | 1.36 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.96 | 2.62 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 1.76 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.71 | 2.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.02 | 3.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24 | 4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.3333 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2230.9866 | 70.9 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2088.5331 | 712 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6311.2166 | 107 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 49814.8166 | 109 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18772.2997 | 393 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 26104.233 | 431 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318 | 90 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1962.9333 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376.25 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.8 | 57 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 504 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 478.4167 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 35914.25 | 97 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 4 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.98 | 1.83 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.01 | 3.89 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.2 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 339.15 | 3.99 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.2 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.5 | 1.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 11132.7328 | 836 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 435 | 290 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 59383.5 | 330 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 307.8 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 42586.1332 | 427 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44602.8 | 872 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253.7499 | 435 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.1663 | 490 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1233.7498 | 315 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400.2 | 87 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 101.6 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 260 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 25141.75 | 57 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1241.3332 | 304 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 87.6 | 36 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 109.25 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.99 | 10.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.99 | 3.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.02 | 4.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 2 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.01 | 2.89 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.02 | 2.93 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.8 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 22.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72 | 12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 1111.8666 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9201.8499 | 183 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1975.8333 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212.6666 | 290 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.55 | 67 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 8.4 | 4.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 611.7167 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 317.9165 | 175 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2289.2999 | 234 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6220.9 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.8 | 1.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.95 | 2.05 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1.5 | 1 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 4 | 9 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.02 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.99 | 1.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.04 | 1.08 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.95 | 1.15 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.01 | 2.43 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.98 | 3.14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.98 | 4.14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 2 | 6 | 12 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 2.5 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.89 | 2.63 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.98 | 1.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.2 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418 | 380 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 146.2 | 102 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 75.6 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 50088.6497 | 417 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 13688.2666 | 112 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6696 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 147.87 | 9.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 200.48 | 9.6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 8 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 79.2 | 17.6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 111.6333 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1736.4667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 3 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 8.4333 | 11 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 60.1333 | 44 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.96 | 1.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1 | 1 | 5 | 43 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1.75 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 1.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.96 | 1.92 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.98 | 5.14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 1.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.94 | 2.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1 | 1 | 8 | 18 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 3 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 2 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.9 | 2.58 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 758.3333 | 70 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2952.2 | 87 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18933.75 | 495 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2009.333 | 440 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72758.2664 | 764 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 49 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 69.55 | 39 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 17657.9998 | 243 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 563.7499 | 165 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 294.95 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 370.17 | 24.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 106 | 21.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 160.875 | 9.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 332.4999 | 150 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 39.9 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.99 | 2.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 19 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.98 | 1.94 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 1 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.02 | 2.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 3.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.98 | 3.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.09 | 1.11 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.97 | 1.69 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 1.32 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.02 | 1.62 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.2 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.01 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.8 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43 | 10.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.75 | 105 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3523.5 | 243 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | WECC | Off-Peak | 571.552 | 33.92 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 6.3 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2323.7497 | 429 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | WECC | Summer | 111.936 | 33.92 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 944.5833 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 683.05 | 57 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 451.1333 | 13.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 272 | 34 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1201.85 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 310 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 858 | 33 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1484.67 | 36.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 504.8333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 234 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 405 | 27 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1110.845 | 16.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 65 | 65 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 539.25 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 555 | 37 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 134.1 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 201.5 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2419.0833 | 55 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 395.4167 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 95.1999 | 204 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 301.75 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 493 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 550 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 130 | 65 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 330 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 576 | 32 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | WECC | Off-Peak | 119.7 | 266 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 3 | 12 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 373.5333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1241.5 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 518.4 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 172.8 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 342.6 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1277.8667 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 581 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 1407.0333 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 54.6 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 12194 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 13006.9333 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 73.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 4379.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1783 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 7824 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 972 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 4 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 34.3 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 316.0667 | 11 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1197 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 4316.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 19.2 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 21.6 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 1437.6 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 2660.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 132.5 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 932.3997 | 378 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.9667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 26 | 78 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 76.45 | 33 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 285.8332 | 245 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 3454.5 | 245 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 70.5667 | 29 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 289.9166 | 245 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 757.0398 | 283.89 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 118.11 | 27.9 | 2 | 2 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6 | 24 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 43.7333 | 64 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 290 | 75 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.1667 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 257.3333 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 82.1332 | 176 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 191.0998 | 234 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 298.2268 | 167.23 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 49.6 | 248 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 249.0833 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 570 | 150 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 251.55 | 193.5 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1530.1332 | 152 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 543.4 | 247 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 787 | 60 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 5457.375 | 192.5 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 250.845 | 167.23 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 476.9165 | 242.5 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 120.8333 | 145 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 388.2082 | 192.5 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 5697.0832 | 275 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 14.25 | 19 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 156.6833 | 119 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1626.3333 | 82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 17.15 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 387.1 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 92.5 | 111 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1485 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 31035.6333 | 82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | SF | Startup Failure | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1333.9999 | 138 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1090.3998 | 282 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 440.1833 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 81.2583 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 98.4083 | 120.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 130.7167 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 122.5 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 472 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1565.05 | 113 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2357.5 | 82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 362.6 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 112.6667 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 805.9626 | 137.38 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 531.0999 | 282 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1434.1833 | 133 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 389.1333 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 172 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 327.9167 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 462.7999 | 267 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 1513.6 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 860-Co-generator Block
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1882.4953 | 52.34 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 6905.0157 | 200.63 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 29422.0223 | 350.61 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 1949.154 | 19.56 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 6671.8525 | 67.11 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 110.192 | 11.36 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 191.4455 | 37.91 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1496.01 | 159.15 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 259.7366 | 116.3 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 1148.42 | 54.6 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 29.6125 | 0.75 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 3332.0751 | 110.03 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1521.8833 | 71.9 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 4932.52 | 155.6 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 250.2683 | 12.41 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 1095.82 | 64.46 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 7463.7 | 248.79 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D3-Forced - Postponed | 200-Nuclear
2010 | Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1390.7783 | 60.91 | 1 | 1 | 2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0 | 0 | 2 | 2 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 4.6497 | 7.54 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3144.0786 | 101.86 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 25.1333 | 13 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 298.08 | 37.26 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 227.52 | 19.2 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0 | 0 | 2 | 3 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 2070.9999 | 327 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1193.5817 | 38.9 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 33.8793 | 11.42 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 86.058 | 20.49 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 968.9708 | 101.11 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 8819.5399 | 305.88 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 12.15 | 14.58 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 445.4333 | 83 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 19.4667 | 14.6 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2474.6574 | 103.47 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 325 | 52 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1238.5576 | 66.47 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 0 | 0 | 2 | 2 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1507.8808 | 99.97 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 844.9 | 34 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1700.5935 | 100.33 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 0 | 0 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 24.3 | 16.2 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 923.3208 | 103.55 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2384.5748 | 100.97 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 84.0147 | 19.24 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 5457.6216 | 219.77 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D2-Forced - Delayed | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 63.8583 | 1.94 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D3-Forced - Postponed | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 4179.3616 | 148.82 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D2-Forced - Delayed | 200-Nuclear
2031 | Fuel preconditioning | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 18.576 | 10.32 | 1 | 1 | 2031-Fuel preconditioning | D1-Forced - Immediate | 200-Nuclear
2035 | Core xenon restrictions | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 12 | 4 | 1 | 1 | 2035-Core xenon restrictions | D1-Forced - Immediate | 200-Nuclear
2035 | Core xenon restrictions | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 560 | 35 | 1 | 1 | 2035-Core xenon restrictions | D1-Forced - Immediate | 200-Nuclear
2035 | Core xenon restrictions | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 16.7333 | 2 | 1 | 1 | 2035-Core xenon restrictions | D1-Forced - Immediate | 200-Nuclear
2035 | Core xenon restrictions | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 67.1 | 3 | 1 | 1 | 2035-Core xenon restrictions | D1-Forced - Immediate | 200-Nuclear
2035 | Core xenon restrictions | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 308.9667 | 23 | 1 | 1 | 2035-Core xenon restrictions | D1-Forced - Immediate | 200-Nuclear
2037 | Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 13301.4053 | 786.29 | 1 | 1 | 2037-Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | D1-Forced - Immediate | 200-Nuclear
2037 | Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 9840.328 | 600.02 | 1 | 1 | 2037-Other fuel limits (use codes 9110 and 9120 for core coastdown; conservation; or stretch) | D1-Forced - Immediate | 200-Nuclear
2040 | Core physics tests | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 10023.7453 | 215.41 | 1 | 1 | 2040-Core physics tests | D1-Forced - Immediate | 200-Nuclear
2040 | Core physics tests | Nuclear Reactor | Core/Fuel | SF | Startup Failure | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 52574.1993 | 987 | 1 | 1 | 2040-Core physics tests | SF-Startup Failure | 200-Nuclear
2060 | Excore nuclear instrumentation | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 200.4467 | 1.07 | 1 | 1 | 2060-Excore nuclear instrumentation | D1-Forced - Immediate | 200-Nuclear
2060 | Excore nuclear instrumentation | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1954.3093 | 746.87 | 1 | 1 | 2060-Excore nuclear instrumentation | D1-Forced - Immediate | 200-Nuclear
2061 | Incore nuclear instrumentation | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Summer | 51136.15 | 521 | 1 | 1 | 2061-Incore nuclear instrumentation | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 138542.53 | 1134.2 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | SF | Startup Failure | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 106647.9 | 821 | 1 | 1 | 2070-Normal refueling | SF-Startup Failure | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 105487.0592 | 1127.4 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 11751.8497 | 759 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 702310.2329 | 1414 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2071 | Refueling equipment problems | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 49313.5996 | 1176 | 1 | 1 | 2071-Refueling equipment problems | U1-Forced - Immediate | 200-Nuclear
2090 | Other core/fuel problems | Nuclear Reactor | Core/Fuel | SF | Startup Failure | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 24175.3497 | 837 | 1 | 1 | 2090-Other core/fuel problems | SF-Startup Failure | 200-Nuclear
2110 | Control rod drive motors | Nuclear Reactor | Control Rods and Drives | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 62759.1992 | 1176 | 1 | 1 | 2110-Control rod drive motors | U1-Forced - Immediate | 200-Nuclear
2112 | Control rod hydraulic drives | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1141 | 7 | 1 | 1 | 2112-Control rod hydraulic drives | D1-Forced - Immediate | 200-Nuclear
2112 | Control rod hydraulic drives | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1374.7692 | 306.64 | 1 | 1 | 2112-Control rod hydraulic drives | D1-Forced - Immediate | 200-Nuclear
2120 | Control rod scram mechanisms | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 6420.576 | 446.39 | 1 | 1 | 2120-Control rod scram mechanisms | D1-Forced - Immediate | 200-Nuclear
2120 | Control rod scram mechanisms | Nuclear Reactor | Control Rods and Drives | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 57165.2 | 964 | 1 | 1 | 2120-Control rod scram mechanisms | U1-Forced - Immediate | 200-Nuclear
2140 | Control rod drive cooling | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 712.8005 | 186.76 | 1 | 1 | 2140-Control rod drive cooling | D1-Forced - Immediate | 200-Nuclear
2150 | Control rod instrumentation | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1595.3 | 43 | 1 | 1 | 2150-Control rod instrumentation | D1-Forced - Immediate | 200-Nuclear
2151 | Control rod drive controls | Nuclear Reactor | Control Rods and Drives | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 70845.8 | 1244 | 1 | 1 | 2151-Control rod drive controls | U1-Forced - Immediate | 200-Nuclear
2151 | Control rod drive controls | Nuclear Reactor | Control Rods and Drives | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 144283.2663 | 1244 | 1 | 1 | 2151-Control rod drive controls | U1-Forced - Immediate | 200-Nuclear
2151 | Control rod drive controls | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 4658.5 | 11 | 1 | 1 | 2151-Control rod drive controls | D1-Forced - Immediate | 200-Nuclear
2155 | Control rod testing | Nuclear Reactor | Control Rods and Drives | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 73545.7663 | 1118 | 1 | 1 | 2155-Control rod testing | U1-Forced - Immediate | 200-Nuclear
2155 | Control rod testing | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 16.8333 | 10 | 1 | 1 | 2155-Control rod testing | D1-Forced - Immediate | 200-Nuclear
2160 | Other control rod drive problems | Nuclear Reactor | Control Rods and Drives | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 68.7885 | 10.89 | 1 | 1 | 2160-Other control rod drive problems | D2-Forced - Delayed | 200-Nuclear
2160 | Other control rod drive problems | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 26998.4 | 286 | 1 | 1 | 2160-Other control rod drive problems | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 36289.6013 | 623.89 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 5024.8916 | 143.5 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 2094.885 | 537.15 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 19002.7183 | 836.51 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 280 | 70 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 26116.3992 | 504.99 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 46946.1183 | 207.1 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 44200 | 85 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 63606.3999 | 422.4 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 55648.1331 | 763 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 10051.4211 | 325.64 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | U3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 76953.6 | 1152 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | U3-Forced - Postponed | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 4276.8 | 396 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 8372.2331 | 371 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 96310.2 | 966 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | U1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 99966.8277 | 837.36 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2220 | Reactor coolant/recirculating pump MG sets | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 1029.4756 | 301.31 | 1 | 1 | 2220-Reactor coolant/recirculating pump MG sets | D1-Forced - Immediate | 200-Nuclear
2230 | Reactor coolant system piping | Nuclear Reactor | Reactor Coolant System | U2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 116468.7493 | 1118.1 | 1 | 1 | 2230-Reactor coolant system piping | U2-Forced - Delayed | 200-Nuclear
2230 | Reactor coolant system piping | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0 | 0 | 1 | 1 | 2230-Reactor coolant system piping | D1-Forced - Immediate | 200-Nuclear
2230 | Reactor coolant system piping | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 13973.0429 | 647.9 | 1 | 1 | 2230-Reactor coolant system piping | D2-Forced - Delayed | 200-Nuclear
2230 | Reactor coolant system piping | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 21106.8 | 343.2 | 1 | 1 | 2230-Reactor coolant system piping | D2-Forced - Delayed | 200-Nuclear
2230 | Reactor coolant system piping | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 3822.0782 | 179.3 | 1 | 1 | 2230-Reactor coolant system piping | D1-Forced - Immediate | 200-Nuclear
2260 | Reactor coolant flanges; fittings; and manways | Nuclear Reactor | Reactor Coolant System | U3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 274338.8 | 1192 | 1 | 1 | 2260-Reactor coolant flanges; fittings; and manways | U3-Forced - Postponed | 200-Nuclear
2260 | Reactor coolant flanges; fittings; and manways | Nuclear Reactor | Reactor Coolant System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 20232.0498 | 501 | 1 | 1 | 2260-Reactor coolant flanges; fittings; and manways | D3-Forced - Postponed | 200-Nuclear
2260 | Reactor coolant flanges; fittings; and manways | Nuclear Reactor | Reactor Coolant System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 462.0663 | 478 | 1 | 1 | 2260-Reactor coolant flanges; fittings; and manways | D3-Forced - Postponed | 200-Nuclear
2290 | Pressurizer spray valves | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 22368 | 699 | 1 | 1 | 2290-Pressurizer spray valves | D1-Forced - Immediate | 200-Nuclear
2290 | Pressurizer spray valves | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 92384.5 | 1165 | 1 | 1 | 2290-Pressurizer spray valves | U1-Forced - Immediate | 200-Nuclear
2300 | Recirculation loop flow control valves | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 68.572 | 24.49 | 1 | 1 | 2300-Recirculation loop flow control valves | D1-Forced - Immediate | 200-Nuclear
2350 | BWR feedwater controls | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 8809.725 | 290.75 | 1 | 1 | 2350-BWR feedwater controls | D2-Forced - Delayed | 200-Nuclear
2350 | BWR feedwater controls | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 11656.1675 | 220.97 | 1 | 1 | 2350-BWR feedwater controls | D2-Forced - Delayed | 200-Nuclear
2390 | Other reactor coolant system instruments and controls | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 25750.5318 | 736.08 | 1 | 1 | 2390-Other reactor coolant system instruments and controls | D1-Forced - Immediate | 200-Nuclear
2400 | Steam generator tube leaks | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1860.1226 | 1052.9 | 1 | 1 | 2400-Steam generator tube leaks | D1-Forced - Immediate | 200-Nuclear
2400 | Steam generator tube leaks | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 31858.5859 | 1159.9 | 1 | 1 | 2400-Steam generator tube leaks | U1-Forced - Immediate | 200-Nuclear
2400 | Steam generator tube leaks | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 812391.2959 | 1145.8 | 1 | 1 | 2400-Steam generator tube leaks | U1-Forced - Immediate | 200-Nuclear
2400 | Steam generator tube leaks | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 16389.606 | 388.84 | 1 | 1 | 2400-Steam generator tube leaks | D1-Forced - Immediate | 200-Nuclear
2400 | Steam generator tube leaks | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 805.0311 | 530.79 | 1 | 1 | 2400-Steam generator tube leaks | D1-Forced - Immediate | 200-Nuclear
2411 | Steam generator tube inspections | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 40881.7566 | 171.4 | 1 | 1 | 2411-Steam generator tube inspections | D1-Forced - Immediate | 200-Nuclear
2421 | Steam generator feedwater nozzles | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 15309.3483 | 28.1 | 1 | 1 | 2421-Steam generator feedwater nozzles | D1-Forced - Immediate | 200-Nuclear
2422 | Other steam generator internals problems | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 5446.08 | 7.32 | 1 | 1 | 2422-Other steam generator internals problems | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 213.547 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 283.48 | 9.12 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 588.4797 | 19.54 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 666.4173 | 14.02 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 1276.1775 | 17.55 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 668.8673 | 10.87 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 892.8878 | 13.33 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 4677.5353 | 9.73 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 385.788 | 24.73 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 690.384 | 9.12 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 1021.635 | 18.66 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 1547.2307 | 6.82 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 3045.6622 | 8.99 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 169.5493 | 11.72 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 235.6275 | 10.59 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 243.78 | 7.17 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 697.9805 | 15.19 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 859.365 | 17.55 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 55.6167 | 7.1 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 527.7907 | 11.72 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 543.2883 | 7.97 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 1727.3327 | 11.72 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 1974.9325 | 15.81 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 114.27 | 11.7 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 1524.465 | 17.1 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 189.875 | 2.94 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 144.5518 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 166.136 | 9.12 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 389.7133 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 1014.8453 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 73.89 | 5.4 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 88.881 | 11.18 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 271.5025 | 11.15 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 179.79 | 11.7 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 187.8217 | 9.47 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 904.5337 | 9.46 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 3814.2275 | 33.65 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 3957.24 | 33.65 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 4769.625 | 11.85 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 147.1367 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 287.9002 | 11.57 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 512.7733 | 10.72 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 610.182 | 18.66 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 712.221 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 1145.078 | 16.79 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 112.7317 | 11.18 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 205.606 | 8.92 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 1767.6467 | 11.15 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 281.388 | 10.48 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 376.7892 | 11.93 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 379.315 | 14.18 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 467.9345 | 17.13 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 286.7767 | 15.16 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 345.66 | 8.4 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 911.6207 | 11.72 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2480 | Other blowdown | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 19448.6595 | 726.6 | 1 | 1 | 2480-Other blowdown | D1-Forced - Immediate | 200-Nuclear
2510 | Main steam isolation valves (BWR and PWR) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 36560.04 | 1107.88 | 1 | 1 | 2510-Main steam isolation valves (BWR and PWR) | D1-Forced - Immediate | 200-Nuclear
2510 | Main steam isolation valves (BWR and PWR) | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 99978.6659 | 1120 | 1 | 1 | 2510-Main steam isolation valves (BWR and PWR) | U1-Forced - Immediate | 200-Nuclear
2510 | Main steam isolation valves (BWR and PWR) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 19145.28 | 870.24 | 1 | 1 | 2510-Main steam isolation valves (BWR and PWR) | D1-Forced - Immediate | 200-Nuclear
2520 | Main steam safety/relief valves (except BWR) | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 67551.6327 | 938 | 1 | 1 | 2520-Main steam safety/relief valves (except BWR) | U1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 7200 | 10 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 26640 | 37 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0 | 0 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 0 | 0 | 1 | 2 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0 | 0 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 14136 | 19 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 744 | 1 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2530 | Atmospheric or condenser dump valves (not SRVs) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3720 | 5 | 1 | 1 | 2530-Atmospheric or condenser dump valves (not SRVs) | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 620.5333 | 35.8 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 11215.633 | 497 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2550 | Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 33619.4994 | 837 | 1 | 1 | 2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | U1-Forced - Immediate | 200-Nuclear
2599 | Other steam generator problems | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 1112.3017 | 46.67 | 1 | 1 | 2599-Other steam generator problems | D1-Forced - Immediate | 200-Nuclear
2599 | Other steam generator problems | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 1894.802 | 46.67 | 1 | 1 | 2599-Other steam generator problems | D1-Forced - Immediate | 200-Nuclear
2600 | High pressure safety injection; core injection; or core spray pumps (including RCIC) | Nuclear Reactor | Core Cooling/Safety Injection | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 101373.5192 | 1172.4 | 1 | 1 | 2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | U1-Forced - Immediate | 200-Nuclear
2600 | High pressure safety injection; core injection; or core spray pumps (including RCIC) | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 10751.8829 | 587 | 1 | 1 | 2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | D1-Forced - Immediate | 200-Nuclear
2602 | Steam turbine drives for high pressure pumps (including RCIC) | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3.0417 | 7.3 | 1 | 1 | 2602-Steam turbine drives for high pressure pumps (including RCIC) | D1-Forced - Immediate | 200-Nuclear
2603 | High pressure piping | Nuclear Reactor | Core Cooling/Safety Injection | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 188564 | 944 | 1 | 1 | 2603-High pressure piping | U1-Forced - Immediate | 200-Nuclear
2603 | High pressure piping | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 1555.1665 | 434 | 1 | 1 | 2603-High pressure piping | D1-Forced - Immediate | 200-Nuclear
2603 | High pressure piping | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 14384.7497 | 489 | 1 | 1 | 2603-High pressure piping | D1-Forced - Immediate | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 113754.1996 | 1158 | 1 | 1 | 2604-High pressure valves | U1-Forced - Immediate | 200-Nuclear
2740 | Containment penetration pressurization system | Nuclear Reactor | Containment System | U2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Winter | 48049.32 | 1174.8 | 1 | 1 | 2740-Containment penetration pressurization system | U2-Forced - Delayed | 200-Nuclear
2770 | Containment cooling system - normal | Nuclear Reactor | Containment System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 39432.9704 | 203.49 | 1 | 1 | 2770-Containment cooling system - normal | D3-Forced - Postponed | 200-Nuclear
2817 | Instruments and controls | Nuclear Reactor | Chemical and Volume Control/Reactor Water Cle | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 361.6866 | 47.8 | 1 | 1 | 2817-Instruments and controls | D1-Forced - Immediate | 200-Nuclear
2830 | Nuclear service water pumps | Nuclear Reactor | Nuclear Cooling Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 257.0878 | 241.02 | 1 | 1 | 2830-Nuclear service water pumps | D1-Forced - Immediate | 200-Nuclear
2890 | Condenser off-gas system problems | Nuclear Reactor | Auxiliary Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 2160 | 45 | 1 | 1 | 2890-Condenser off-gas system problems | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1689.6 | 192 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3306 | 435 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1620 | 75 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5048.95 | 419 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 52655.5 | 53 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2280 | 380 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 239.6836 | 135.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 40298.7498 | 309 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9126.0664 | 373 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15693.6999 | 363 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54819.5831 | 745 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15030.0665 | 524 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3730.1333 | 208 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19543.7 | 163 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1239.3333 | 110 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1350 | 75 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3770.8 | 44 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 454.4895 | 245.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1611.7312 | 265.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3583.4332 | 337 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 597.7969 | 245.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1138.2709 | 245.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4108.333 | 500 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17904 | 373 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18744.1332 | 532 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2471.9999 | 90 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1416.8 | 253 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3160.9999 | 174 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22937.2664 | 388 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1618.7999 | 171 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 441.4 | 441.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1270.7881 | 265.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7139.3979 | 407.19 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4719.2665 | 315.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179718 | 770 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10059.8 | 179 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20794.5832 | 325 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32349.145 | 310.9 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 17531.25 | 75 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4523.5666 | 169 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6430.5333 | 136 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 4907.35 | 147 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5396.95 | 299 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 383.3333 | 100 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4649.9999 | 90 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 644.1646 | 235.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2130.7725 | 315.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 9364.5833 | 156.25 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18240.0833 | 113 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8706.25 | 175 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1291.9998 | 228 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3153.75 | 435 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4357.2497 | 435 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 876 | 90 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1658.7 | 114 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5853.5 | 115 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1488.2133 | 174.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2115 | 30 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6390.7664 | 427 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 741.8245 | 315.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 742.14 | 111.6 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1742.2034 | 185.67 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4180.4165 | 395 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68969.4331 | 622 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2635.4166 | 125 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3017.25 | 405 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3617.944 | 411.13 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 813.75 | 93 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4757.3164 | 337 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2771.4032 | 437.59 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1416.6666 | 100 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 12025.2498 | 309 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4509.9166 | 299 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3763.2333 | 58 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27444.2999 | 234 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 16729.6665 | 310 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7024.7666 | 169 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2610 | 435 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3829.3331 | 320 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9796.95 | 369 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1189.0235 | 315.67 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1454.7164 | 337 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 580.9666 | 174.29 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2478.9333 | 112 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 400 | 100 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21159.9996 | 600 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 365.4475 | 20.55 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 480.4333 | 58 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4125 | 90 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8447.0832 | 475 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 266.4 | 266.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 288.7465 | 541.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4264.4331 | 338 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 475.3 | 135.8 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4551.25 | 75 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 879.2 | 112 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93662.5 | 635 | 1 | 1 | 3110-Condenser tube leaks | SF-Startup Failure | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10710.1666 | 179 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10190.7164 | 773 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 27280.595 | 160.9 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3.6833 | 8.5 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 7.6 | 8 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 26067.6199 | 217.2 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 158.34 | 36.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 8445.25 | 83 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 43.84 | 4.8 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 49.8333 | 23 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 16.1333 | 8 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 38.7167 | 23 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 15950.5 | 138 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 861.77 | 18.2 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 4208.5766 | 44.2 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 59372.2497 | 387 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | PC | 650 | Fluidized Bed | RFC | Winter | 769 | 60 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1508.75 | 51 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 656.4333 | 47 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 1399.4999 | 270 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 1480.4999 | 270 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 262.0833 | 37 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 218.8667 | 13.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 170.6033 | 40.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 13308.9 | 218 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 534.39 | 42.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 788.3417 | 38.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 3311.9998 | 270 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 179.35 | 51 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 96.0483 | 40.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 578.805 | 42.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 800-Miscellaneous
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 863.5 | 30 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Off-Peak | 6369.3319 | 98.04 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 4284 | 272 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 3681.6 | 236 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5597.0663 | 556 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 0 | 0 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 14778.8333 | 247 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4052.5 | 75 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 852-CC steam units
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.1666 | 58 | 1 | 1 | 3111-Condenser tube fouling shell side | U1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 145 | 15 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2658.3333 | 58 | 1 | 1 | 3111-Condenser tube fouling shell side | U1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3440 | 16 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1665 | 185 | 1 | 1 | 3111-Condenser tube fouling shell side | D2-Forced - Delayed | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Off-Peak | 453.3332 | 170 | 1 | 1 | 3111-Condenser tube fouling shell side | U1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.35 | 103 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 821.6666 | 85 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.6 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.8333 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.15 | 53 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 57 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.25 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.3333 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.9 | 63 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.75 | 95 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.2166 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.6 | 84 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.3333 | 68 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 478.3333 | 70 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1157.3332 | 280 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 938 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 29.05 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 27230.8 | 152 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 9 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1832.9164 | 415 | 1 | 1 | 3112-Condenser tube fouling tube side | U1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.91663 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.9999 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165 | 66 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 385.2083 | 107.5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 788.0333 | 94 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.8 | 26 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.4167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6667 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.5167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.9333 | 47 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.3333 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136.1667 | 19 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2031.6667 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 49.8333 | 115 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 717.9333 | 44 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23139.7999 | 222 | 1 | 1 | 3112-Condenser tube fouling tube side | U2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 40 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.0166 | 73 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.5 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1739.5667 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.8333 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.4167 | 41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.4167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45 | 90 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.5 | 14 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.5 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.5 | 85 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79 | 79 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.95 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214.55 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 448.3333 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 718.75 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1232.9166 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2960.1 | 143 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4314.7583 | 42.65 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 248.5 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 643.8997 | 411 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 0.93332 | 28 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.9166 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.2 | 64 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.4166 | 85 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.6166 | 73 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.3333 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 502 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810.8333 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 869.9166 | 65 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 12 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.75 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.0833 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.8333 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.5 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.25 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169.5833 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 373.0333 | 62 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 145 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12665.3333 | 118 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.45 | 81 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136.7933 | 3.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 549.0833 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 784.6666 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 861.25 | 65 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.6666 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.3333 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.9333 | 79 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 49 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.6666 | 80 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.25 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.6 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 253.5866 | 41.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 353.8 | 58 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.5366 | 41.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371.25 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3482.5 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.6667 | 1 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 10.2666 | 28 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.6667 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.1833 | 83 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 641.6666 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.3333 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.75 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.4167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.3333 | 86 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 80 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.85 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418.5 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 736.6 | 58 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5080.1667 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.3333 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 221.5667 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 24.5 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 36 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 156.3333 | 28 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1971.2 | 128 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 419.25 | 215 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1524.57 | 5.71 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 333 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 5528.2 | 524 | 1 | 1 | 3112-Condenser tube fouling tube side | SF-Startup Failure | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.25 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 166.6666 | 80 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 531 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 771.6 | 72 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 788.3333 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.6 | 12 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3333 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.0833 | 41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.8667 | 7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.5 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 15 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.5167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.9333 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.6 | 72 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.6667 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.75 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.5 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 339.6167 | 41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1430 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2377.5333 | 76 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1846.6666 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2.3333 | 28 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 144.9 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.94 | 3.71 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.03 | 8.29 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 40824 | 243 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455.0333 | 73 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 620.83 | 1.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.4 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5 | 5 | 1 | 2 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.6167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.4 | 52 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.3333 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.3333 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.1333 | 61 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135.3333 | 58 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.7667 | 23.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.9999 | 111 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4328.775 | 47.7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9149 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1320.8333 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 294.5 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 21.3333 | 40 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 161.6667 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 186.9 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 900 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 48 | 2 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 13315.4 | 21 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 0 | 0 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 263 | 1 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 247.38 | 55.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2232 | 3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 110.3333 | 2 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2496 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 6084 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 864 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0 | 0 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 21432 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 94.0333 | 40.3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 42 | 28 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 45 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 35.35 | 30.3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 116.7833 | 49 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 76.14 | 42.3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 75.2 | 48 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 800-Miscellaneous
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 84 | 14 | 2 | 2 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 2022.9997 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1530 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1566 | 522 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 513.2998 | 522 | 1 | 2 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1402.5 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 2079.2998 | 522 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 15.54 | 14.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4.48 | 4.2 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 2031.4998 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 14254.5 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 2079.2998 | 522 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 7849.4483 | 17.9 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1470.4998 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 2031.4998 | 510 | 1 | 2 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1530 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 2031.4998 | 510 | 1 | 2 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1035.6666 | 260 | 1 | 2 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1083.4666 | 272 | 1 | 2 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 2031.4998 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U2-Forced - Delayed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1632 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 2040 | 510 | 1 | 2 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 31.11 | 5.1 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1155.9997 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 501.4998 | 510 | 1 | 5 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1530 | 510 | 1 | 1 | 3112-Condenser tube fouling tube side | U3-Forced - Postponed | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2222.8733 | 21.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 837 | 93 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1116 | 93 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 4916.5999 | 93 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30 | 30 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 8237.5 | 659 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 398.6666 | 130 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 69432.5333 | 136 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 710.6666 | 130 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7459.2 | 222 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.9667 | 38 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.5 | 15 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.858 | 5.18 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 982.5 | 327.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1998.05 | 449 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2112.75 | 135 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2730.4831 | 419 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 292.5 | 130 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1085.8497 | 513 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 836.5999 | 267 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 649.5416 | 327.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5679.9996 | 600 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2048.5832 | 155 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2952 | 369 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.4998 | 375 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 6193.0999 | 102 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 446.5833 | 23 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 683.7 | 106 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1739.85 | 21 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5071.0832 | 155 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1427.8498 | 513 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 14.25 | 57 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 12.28 | 49.12 | 1 | 2 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 7.3067 | 0.64 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 650-Fluidized Bed
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 630.6166 | 157 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 800-Miscellaneous
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 3566.6667 | 16 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3.25 | 13 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 956.5 | 30 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 228.6666 | 28 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 63.0666 | 88 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 982.5 | 30 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 113.1 | 78 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 16.6 | 83 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 181.9999 | 168 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 542.0167 | 17 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 135.88 | 94.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 125.1466 | 98.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 799.3332 | 218 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 138.32 | 98.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 175.38 | 94.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1.2097 | 0.38 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2.0032 | 1.19 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3.08 | 2.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1.421 | 0.58 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2.9603 | 1.07 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 10.24 | 7.68 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2.451 | 1.29 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3.456 | 7.68 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 6.4093 | 5.06 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 7.5987 | 2.78 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 0.247 | 0.19 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2.4917 | 5.98 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1.98 | 2.64 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5.8 | 4.35 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 11.3493 | 5.12 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 14.6933 | 5.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4.454 | 2.62 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2.665 | 6.15 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2.0528 | 1.09 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3.096 | 1.29 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9.955 | 5.43 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 15.3813 | 7.21 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2.1463 | 0.94 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4.8167 | 4.25 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9.1858 | 7.55 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 17.7688 | 7.67 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 23.9143 | 5.54 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1841.6666 | 85 | 1 | 1 | 3114-Air-cooled condenser tubes | U1-Forced - Immediate | 100-Fossil-Steam
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 14.7 | 6 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 850-Combined Cycle Block
3115 | Air-cooled condenser pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1048.6915 | 515.75 | 1 | 1 | 3115-Air-cooled condenser pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3115 | Air-cooled condenser pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 189.75 | 189.75 | 1 | 1 | 3115-Air-cooled condenser pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.75 | 3 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 100-Fossil-Steam
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 7 | 14 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 103.5 | 23 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8.5 | 17 | 1 | 2 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 51 | 10 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 156 | 26 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3597.2 | 6 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 420.6398 | 286.8 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 19 | 19 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3117 | Air-cooled condenser fan motors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 0 | 0 | 1 | 1 | 3117-Air-cooled condenser fan motors | D1-Forced - Immediate | 851-CC GT units
3117 | Air-cooled condenser fan motors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 177.4999 | 213 | 1 | 1 | 3117-Air-cooled condenser fan motors | U1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 407.6 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 100-Fossil-Steam
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 907.68 | 37.82 | 1 | 1 | 3118-Other Air-cooled condenser problems | D2-Forced - Delayed | 650-Fluidized Bed
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 216 | 18 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 800-Miscellaneous
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.6 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.96667 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.25 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.8 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.55 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.9 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.0333 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.3333 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.9 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.1333 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.95 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.1 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.25 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 14.5 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 14.5667 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15.6333 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 44.2 | 52 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 53.1 | 27 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 99.75 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 128 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.1333 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.5 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.8667 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2 | 4 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.75 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.8333 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4 | 8 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.9167 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.5 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.4 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.6667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13.8 | 23 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 17.85 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 25.8667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 30.3333 | 26 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 40.7333 | 26 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 44 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.45 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.4667 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.25 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7.0833 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 16.5 | 18 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18.3667 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18.9333 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 21.6 | 18 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 22.1 | 26 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 23.3333 | 28 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 33.3333 | 25 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 39.7333 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 42.2333 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 61.8 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 153.6 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 406.6665 | 488 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0 | 0 | 1 | 5 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.4 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.0833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.65 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.7333 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.0667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.4167 | 41 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.0833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.7 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.75 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7.4667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7.5 | 9 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9.6 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.5 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 13 | 65 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 16.8 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 19.25 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 23.2 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 28.6667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 33 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 35.2 | 33 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 38.5 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.75 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.8333 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.4667 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.4667 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.55 | 37 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9.9167 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 12.1833 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13.9333 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 17.25 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 21.4 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 37.5667 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 79.2 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 83.5 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 85.6833 | 53 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 87.75 | 39 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 101.7833 | 31 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 25.85 | 33 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 67.1666 | 31 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.28332 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.33333 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.43332 | 26 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.1 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.9667 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.2 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.3333 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.15 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.3333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.6167 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.8 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.1333 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.9167 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 16.3333 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 16.4833 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 29.5833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 42.4666 | 28 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 69.6833 | 37 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 137.8667 | 44 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 214.7 | 57 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 888.3329 | 650 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | MRO | Summer | 36 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.2333 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.0667 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.15 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.5667 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.6833 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.9167 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.1 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.3333 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.4 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.4 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.4333 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.1333 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.2833 | 29 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7.6667 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9.3 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9.6 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.8333 | 25 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.2 | 56 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.55 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 12.2667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 23 | 46 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 50 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | MRO | Summer | 60.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | MRO | Summer | 61.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 0.15 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.3 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.6 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.75 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5.6 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.3 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.2667 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.7333 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.2 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11.8833 | 31 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 22.1667 | 38 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 22.75 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 23.3333 | 25 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 24.4 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 28.6 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 33.6 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 50.5 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 55 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 63 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 3185.6665 | 190 | 1 | 1 | 3118-Other Air-cooled condenser problems | U1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 298.35 | 221 | 1 | 1 | 3118-Other Air-cooled condenser problems | U1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 33.6 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 404.9166 | 215 | 1 | 1 | 3118-Other Air-cooled condenser problems | U1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 43.8667 | 47 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 58 | 29 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1207.2 | 72 | 1 | 1 | 3118-Other Air-cooled condenser problems | U1-Forced - Immediate | 852-CC steam units
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6955.1666 | 290 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | U1-Forced - Immediate | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 637.1 | 277 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 612.3366 | 262.43 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | SF-Startup Failure | 851-CC GT units
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 805.923 | 282.78 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | U1-Forced - Immediate | 852-CC steam units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13569.9996 | 600 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 161926.49 | 438.35 | 1 | 1 | 3120-Tube sheets | D1-Forced - Immediate | 200-Nuclear
3120 | Tube sheets | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 22864.7567 | 403.14 | 1 | 1 | 3120-Tube sheets | D1-Forced - Immediate | 200-Nuclear
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 259091.5 | 955 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 850-Combined Cycle Block
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510.3333 | 20 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2321.9 | 14 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.3333 | 20 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.6667 | 10 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 934.1333 | 4 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1189.1333 | 4 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.25 | 15 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 5151.0666 | 56 | 1 | 1 | 3121-Expansion joint | U1-Forced - Immediate | 830-Geothermal
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 49.3 | 34 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 830-Geothermal
3121 | Expansion joint | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 19 | 38 | 1 | 1 | 3121-Expansion joint | U1-Forced - Immediate | 850-Combined Cycle Block
3121 | Expansion joint | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 47597.9663 | 502 | 1 | 1 | 3121-Expansion joint | U1-Forced - Immediate | 850-Combined Cycle Block
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 158.1298 | 338.85 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 850-Combined Cycle Block
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 27.6666 | 41.5 | 2 | 2 | 3121-Expansion joint | D1-Forced - Immediate | 851-CC GT units
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 53.2167 | 51.5 | 2 | 2 | 3121-Expansion joint | D1-Forced - Immediate | 851-CC GT units
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 146.2166 | 141.5 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 852-CC steam units
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 84.3332 | 126.5 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 852-CC steam units
3122 | Gaskets and seals | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5963.0999 | 234 | 1 | 1 | 3122-Gaskets and seals | SF-Startup Failure | 100-Fossil-Steam
3122 | Gaskets and seals | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2201 | 310 | 1 | 1 | 3122-Gaskets and seals | D1-Forced - Immediate | 850-Combined Cycle Block
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 1103.99 | 83.32 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 851-CC GT units
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3874.8233 | 157.3 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 851-CC GT units
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 856.2666 | 152 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 851-CC GT units
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3906.2833 | 157.3 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 851-CC GT units
3122 | Gaskets and seals | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2618 | 68 | 1 | 1 | 3122-Gaskets and seals | D1-Forced - Immediate | 852-CC steam units
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 5497.4999 | 225 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 852-CC steam units
3123 | Hot well | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1890 | 270 | 1 | 1 | 3123-Hot well | D1-Forced - Immediate | 100-Fossil-Steam
3123 | Hot well | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5176.2666 | 329 | 1 | 1 | 3123-Hot well | D1-Forced - Immediate | 100-Fossil-Steam
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 3.15 | 27 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 830-Geothermal
3123 | Hot well | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1009.0664 | 352 | 1 | 1 | 3123-Hot well | D1-Forced - Immediate | 850-Combined Cycle Block
3123 | Hot well | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 131.2333 | 127 | 1 | 1 | 3123-Hot well | D1-Forced - Immediate | 851-CC GT units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 37.2 | 46.5 | 3 | 3 | 3123-Hot well | U1-Forced - Immediate | 851-CC GT units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 372.4666 | 151 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 851-CC GT units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 47.275 | 46.5 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 851-CC GT units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 131.7498 | 255 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 852-CC steam units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 310.7999 | 126 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 852-CC steam units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 876.85 | 39 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 288.75 | 21 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 428.25 | 15 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 200-Nuclear
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 9.25 | 3 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 200-Nuclear
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 509.0665 | 368 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1155 | 231 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 2031.4998 | 510 | 1 | 1 | 3124-Tube sheet fouling | U3-Forced - Postponed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 496.3999 | 219 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 523.5998 | 231 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 501.4998 | 510 | 1 | 1 | 3124-Tube sheet fouling | U2-Forced - Delayed | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 525.6665 | 380 | 1 | 1 | 3124-Tube sheet fouling | D2-Forced - Delayed | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53874.9662 | 691 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U3-Forced - Postponed | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9933.2999 | 162 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.7167 | 13 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 26372.8333 | 79 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228 | 72 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1561.77 | 120.6 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136.8 | 72 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1446.7 | 102 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14569.0664 | 472 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 722.4 | 72 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885.5 | 77 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 495.6 | 72 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 805.9308 | 110.15 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.8833 | 59 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 6814.1664 | 325 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 337.4999 | 162 | 2 | 2 | 3130-Air ejectors | U1-Forced - Immediate | 851-CC GT units
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 316.6666 | 152 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 852-CC steam units
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.6666 | 80 | 1 | 1 | 3131-Air ejector piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1231.4848 | 495.9 | 1 | 1 | 3131-Air ejector piping and valves | SF-Startup Failure | 100-Fossil-Steam
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1722.1 | 102 | 1 | 1 | 3131-Air ejector piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 504.6 | 58 | 1 | 1 | 3131-Air ejector piping and valves | U1-Forced - Immediate | 830-Geothermal
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 597.6 | 72 | 1 | 1 | 3131-Air ejector piping and valves | U3-Forced - Postponed | 830-Geothermal
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 589.197 | 280.57 | 1 | 1 | 3131-Air ejector piping and valves | SF-Startup Failure | 850-Combined Cycle Block
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 53417.7 | 183 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 852-CC steam units
3132 | Inter and after condensers | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6966.2999 | 99 | 1 | 1 | 3132-Inter and after condensers | U1-Forced - Immediate | 100-Fossil-Steam
3132 | Inter and after condensers | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 840 | 30 | 1 | 1 | 3132-Inter and after condensers | D1-Forced - Immediate | 862-CoG steam units
3132 | Inter and after condensers | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 4445 | 35 | 1 | 1 | 3132-Inter and after condensers | D1-Forced - Immediate | 862-CoG steam units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3945.7 | 422 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 803.4665 | 524 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.9497 | 429 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 955.5 | 91 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 147.7338 | 63.77 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 850.6663 | 580 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 740.6665 | 404 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 507.5 | 105 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15988.5 | 855 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9954.692 | 205.04 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3291.75 | 855 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 281.0169 | 285.78 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 18.9 | 21 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 820.729 | 180.38 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 101.43 | 44.1 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 77.49 | 86.1 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 355.04 | 126.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 16.6 | 2 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 337.0266 | 128.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 200-Nuclear
3133 | Vacuum pumps | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1816 | 160 | 1 | 1 | 3133-Vacuum pumps | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 16.2 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 17.9666 | 49 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 154.4 | 16 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 120.0833 | 55 | 1 | 1 | 3133-Vacuum pumps | U3-Forced - Postponed | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 41.4 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 26.1 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 156.3332 | 140 | 2 | 2 | 3133-Vacuum pumps | D1-Forced - Immediate | 851-CC GT units
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 122.8333 | 110 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 851-CC GT units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 517.9999 | 210 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 852-CC steam units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 295.9165 | 265 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 852-CC steam units
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1371.133 | 524 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 58571.3332 | 140 | 1 | 1 | 3134-Vacuum pump piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 167.5738 | 73.39 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 852-CC steam units
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 375.3 | 139 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | U1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4646.25 | 531 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 364.1916 | 150.7 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4737.5 | 125 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.0674 | 194.85 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 394.855 | 47.1 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 888.5665 | 437 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 378.7733 | 169.6 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | U1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 158.5 | 30 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 100-Fossil-Steam
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 214.1332 | 292 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 100-Fossil-Steam
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 97744.0163 | 1247 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 200-Nuclear
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 16.2 | 6 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 650-Fluidized Bed
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 219.3333 | 28 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 650-Fluidized Bed
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3646.5 | 429 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 650-Fluidized Bed
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 98.9333 | 16 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 650-Fluidized Bed
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6577.9999 | 429 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 650-Fluidized Bed
3139 | Other air extraction system problems - general | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 86.35 | 157 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 800-Miscellaneous
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1284.9833 | 236.5 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 850-Combined Cycle Block
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 203.1666 | 230 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 91.3333 | 40 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 943 | 230 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 140.0666 | 191 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 101.6667 | 50 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 180 | 120 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 601.9999 | 120 | 1 | 1 | 3139-Other air extraction system problems - general | SF-Startup Failure | 852-CC steam units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 123.6665 | 265 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 852-CC steam units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 205.9999 | 120 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 893.464 | 34.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 43 | 5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 431.6666 | 70 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 581.8586 | 68.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6174 | 490 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6361.9666 | 34 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17647.5 | 325 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 314.5999 | 156 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 61 | 122 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.3867 | 8.8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 73273.2665 | 211 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13556.2 | 336.8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 59.5 | 102 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.7166 | 163 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12300 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 6.8 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.6663 | 475 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 98.5999 | 102 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 44.8 | 64 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 306.1666 | 167 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 786.25 | 37.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4707.0833 | 27.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4764.6666 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 813.4499 | 153 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2808.05 | 497 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6618.3328 | 836 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4415.4 | 446 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6853.533 | 446 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5102.6665 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84.4233 | 53.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115.5 | 9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 83014.4 | 128 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 403.3333 | 220 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1762.4997 | 450 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 89.7 | 69 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1859.1807 | 39.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 775.9997 | 480 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 781.76 | 44.8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3297.9167 | 12.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6971.532 | 63.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7464.9999 | 300 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 457.0833 | 25 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 449.6666 | 142 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2039.04 | 566.4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33280 | 650 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 896 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1223.1313 | 63.32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 52.7767 | 14.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4400 | 400 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9735.2666 | 94 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2640.3664 | 758 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8989.75 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16.3333 | 5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1509.75 | 165 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6401 | 740 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6966.6664 | 836 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3625.232 | 174.29 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 200-Nuclear
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 15.6 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 142.72 | 35.68 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 25.252 | 25.68 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 56.1 | 102 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Other | BM | 800 | Miscellaneous | SERC | Winter | 22.1 | 19.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 800-Miscellaneous
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 4910 | 5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 230.0666 | 58 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 15.6 | 39 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 7.8833 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 61.7666 | 34 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 294.4 | 256 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 91.9999 | 240 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 111.7831 | 353 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 4.5332 | 272 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 1087.3332 | 233 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 325.6 | 148 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 732.6665 | 280 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 21277.2 | 894 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Winter | 398.9332 | 272 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 317.7 | 353 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 132.55 | 241 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 725.3498 | 267 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 25002.6665 | 256 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 6 | 40 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 247.9999 | 240 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 425.3333 | 110 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1351.1166 | 156.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 13631.8333 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 498 | 120 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 372.3 | 36.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 43.3333 | 4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 115.5 | 110 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 2075.8833 | 169 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 189.5666 | 242 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 193.4833 | 247 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 222.7166 | 161 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 44.1 | 147 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 539.2833 | 247 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 607.2 | 253 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 86.6667 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 191.3332 | 140 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 4.1165 | 247 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 592.8 | 247 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 65 | 6 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 60.5 | 242 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 225.8666 | 242 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 129.75 | 173 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 230.5333 | 247 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1014.3 | 161 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 112.6999 | 147 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 157.586 | 121.22 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 219.2665 | 253 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 33.09 | 110.3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1593.5332 | 212 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 3380.0333 | 31 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 2.1499 | 129 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Summer | 173.8 | 158 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1263.3165 | 229 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1374 | 229 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 36.1667 | 7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 487.6 | 212 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 103.05 | 229 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 149.7705 | 103.29 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2303 | 188 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 169.8499 | 129 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 237.9999 | 255 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 1392.4166 | 31 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 224.1666 | 269 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 31.5 | 126 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 116.1666 | 85 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 16840.5997 | 483 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 80.1209 | 282.78 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 169.1667 | 25 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 161.5 | 170 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 199.7499 | 255 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 616.8 | 257 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 13339.9999 | 174 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 144.2998 | 234 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 222.7332 | 257 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 20.1667 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 860-Co-generator Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 6903 | 236 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 862-CoG steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 7153.25 | 71 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 862-CoG steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 127.5999 | 264 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 862-CoG steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 134.4 | 64 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2062.5 | 330 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1163.8766 | 216.2 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 9150 | 75 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6521.6664 | 430 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2316.6665 | 500 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2118.75 | 339 | 1 | 1 | 3150-Hot well level controls | SF-Startup Failure | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 300.8 | 64 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 225.89 | 46.1 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 650-Fluidized Bed
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 84.5333 | 8 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 650-Fluidized Bed
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 267.4 | 42 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 412.7666 | 61 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 91.7 | 42 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 202.8 | 39 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 435.4 | 42 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 70.85 | 39 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 267.3833 | 61 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 3.6 | 27 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 4906.6665 | 256 | 2 | 2 | 3150-Hot well level controls | U1-Forced - Immediate | 851-CC GT units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 5457.5331 | 284 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 506.8498 | 279 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 53.95 | 83 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 88.5333 | 83 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 103.75 | 83 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 24.2 | 121 | 1 | 1 | 3151-Vacuum pump and air ejector controls | D1-Forced - Immediate | 100-Fossil-Steam
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.1 | 151 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 100-Fossil-Steam
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 148.3777 | 12.61 | 1 | 1 | 3151-Vacuum pump and air ejector controls | D1-Forced - Immediate | 650-Fluidized Bed
3152 | Air-cooled condenser controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 61.0665 | 229 | 1 | 1 | 3152-Air-cooled condenser controls | U1-Forced - Immediate | 851-CC GT units
3152 | Air-cooled condenser controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 40.0666 | 150.25 | 1 | 1 | 3152-Air-cooled condenser controls | D1-Forced - Immediate | 852-CC steam units
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64 | 10 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 171 | 342 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 214.1332 | 292 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 316.6665 | 380 | 1 | 1 | 3159-Other condensing system controls and instruments | SF-Startup Failure | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1743.4 | 379 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1344 | 280 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5026.4 | 824 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 79056 | 9 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 200-Nuclear
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1508.75 | 85 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 650-Fluidized Bed
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 356.3 | 42 | 1 | 1 | 3159-Other condensing system controls and instruments | SF-Startup Failure | 830-Geothermal
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 22.8666 | 28 | 2 | 2 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 851-CC GT units
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 67.7833 | 83 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 852-CC steam units
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 48.3 | 322 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 852-CC steam units
3170 | Condenser inspection (use code 3110 to report looking for tube leaks) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6050.55 | 193 | 1 | 1 | 3170-Condenser inspection (use code 3110 to report looking for tube leaks) | U1-Forced - Immediate | 100-Fossil-Steam
3170 | Condenser inspection (use code 3110 to report looking for tube leaks) | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2020 | Other | BM | 800 | Miscellaneous | WECC | Summer | 1288.0833 | 29 | 1 | 1 | 3170-Condenser inspection (use code 3110 to report looking for tube leaks) | U2-Forced - Delayed | 800-Miscellaneous
3170 | Condenser inspection (use code 3110 to report looking for tube leaks) | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 188.55 | 419 | 1 | 1 | 3170-Condenser inspection (use code 3110 to report looking for tube leaks) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
3180 | Major condenser overhaul | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6667 | 10 | 1 | 1 | 3180-Major condenser overhaul | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 85.75 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 274 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 452.8 | 48 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.38332 | 23 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 107.25 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4125 | 625 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | U1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 591.25 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 43.5 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 58.5 | 13 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 200 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 314.6666 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 97.8 | 18 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 232.5 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.66664 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 384 | 48 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 226.8 | 63 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 99.75 | 35 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 105 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 444.8 | 48 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 242.6666 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.3333 | 55 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 62.2667 | 8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 481.5 | 30 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1137.35 | 13.8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1797.84 | 36.32 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 127.2667 | 23 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 226.6667 | 50 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 264.6666 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3181.6599 | 148.56 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 124.9667 | 23 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 222.0833 | 25 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.6666 | 40 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9946.5 | 57 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 69.5 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 155.5166 | 43 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 223.8666 | 92 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28441.5 | 849 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | SF-Startup Failure | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 17618.6666 | 160 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 59512.8 | 72 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.33333 | 5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 147.446 | 20.67 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 407.8666 | 92 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 831.0666 | 92 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9269.8667 | 32 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.46667 | 2 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45308.9998 | 495 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 180.4 | 66 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 374.1333 | 92 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 437 | 92 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.25 | 3 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 30 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26721.85 | 137 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.8 | 36 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24210.0832 | 245 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1.8667 | 7 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 5201 | 7 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 800-Miscellaneous
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 581.0165 | 491 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 55.5333 | 68 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 97238.5329 | 668 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3414.3082 | 156.5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 17445.9999 | 165 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 43669.7999 | 162 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1104.6 | 31.5 | 2 | 2 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1316.0083 | 39.5 | 2 | 2 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 235 | 47 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 41120.1666 | 170 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 852-CC steam units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2148.925 | 64.5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 852-CC steam units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 24631.25 | 75 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 852-CC steam units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4260.5999 | 121.5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9.35 | 51 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.3333 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2061.6666 | 100 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 11.5 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 43.5 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 117.3 | 23 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 157.5 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 213.3333 | 40 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 647.5 | 70 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2570.6666 | 128 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2077.65 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 117.3667 | 50.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 30 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.25 | 45 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 78 | 45 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 79.9167 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 82.8333 | 70 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 200 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 678.3333 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2037.6833 | 103 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 34.4167 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 69.5833 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428.75 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4890 | 489 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 59.4167 | 23 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 62.0833 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 85 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 326.5 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 849.3332 | 140 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1992.1498 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2154.6 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 16991.5666 | 103 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4.1666 | 125 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 28.3333 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 30 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 100.6667 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 224 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 566.5 | 103 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2032.5333 | 103 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2570.6666 | 128 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2507.959 | 332.18 | 1 | 1 | 3199-Other miscellaneous condensing system problems | SF-Startup Failure | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 169.8666 | 28 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 493.5 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 494.1667 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2052 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2434.25 | 749 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.3333 | 70 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 169.6716 | 53.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 22.9167 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 61.5 | 30 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2510.9332 | 128 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2537.1666 | 130 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2094.7498 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 705.6666 | 145 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 36.6666 | 40 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 70.4167 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 98.3333 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 275 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 328 | 32 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 677.5 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 45155.3999 | 153 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1547.5497 | 513 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D3-Forced - Postponed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 709.1 | 42 | 1 | 1 | 3199-Other miscellaneous condensing system problems | SF-Startup Failure | 830-Geothermal
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 358.0333 | 46 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 94.3 | 138 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1074.15 | 279 | 1 | 1 | 3199-Other miscellaneous condensing system problems | SF-Startup Failure | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 4.125 | 49.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 56.925 | 126.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 187.32 | 156.1 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 189.9216 | 156.1 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 31.785 | 48.9 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 197.6 | 152 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Summer | 8215.9 | 66 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Summer | 187.7332 | 128 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Winter | 3293.5332 | 508 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9.4208 | 22.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 36.522 | 182.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 47.0005 | 122.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.5 | 50 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 222.3923 | 242.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 529.8332 | 170 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2271.25 | 115 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5755.4164 | 475 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 23487.28 | 42.86 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73.8 | 41 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 284.8999 | 111 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 496 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1173.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4537.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 9883.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6656 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 227.0665 | 524 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 31964.4336 | 142.18 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 127563.905 | 82.18 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1076.8333 | 130 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4477.8332 | 134 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5709.6 | 237.9 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 847.4666 | 227 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 17.1016 | 102.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357.0166 | 31 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4032.7999 | 213 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 998.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1825 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7776.1666 | 97 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3810 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 471.45 | 449 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3764.5333 | 76 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 58558 | 38 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 108389.65 | 111 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 1255 | 75 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 14712.1667 | 41 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6968 | 520 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9858.1166 | 263 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3541.9999 | 138 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6851.3698 | 34.67 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.9166 | 115 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 28.522 | 142.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238 | 170 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 296.8133 | 222.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 462.8 | 35.6 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 747.5 | 115 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7465.9999 | 120 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330.5999 | 171 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 856.9 | 41 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 275 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 295 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3903.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5789.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 500 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5159 | 77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7161 | 77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 40261.6666 | 49 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 7601.5333 | 39.2 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 28354.2999 | 78 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 273 | 21 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19684.224 | 97.64 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152 | 190 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 329 | 140 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17260 | 80 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 705 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5089.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4905 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 17015.972 | 132.18 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 27566 | 179 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 220322.8 | 536 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2281.8 | 6 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2670.2728 | 20.11 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10252 | 110 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 25.044 | 62.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 25.6525 | 102.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 100 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.25 | 75 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 92.1456 | 162.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385 | 70 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6234.15 | 117 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14472 | 45 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52462.3259 | 178.92 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79636.2 | 268 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112525.2 | 302 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1548.0166 | 317 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 396 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 459 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1049.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2895 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10728.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 26962.8332 | 385 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 920 | 115 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6623.3998 | 684 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2030 | 50 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8575 | 49 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5 | 90 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 23.6377 | 202.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 90 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.9166 | 65 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170 | 75 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 50 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 413.3332 | 200 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 575 | 115 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8093.3966 | 85.72 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10577.9999 | 180 | 2 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20802.1666 | 65 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26916.9 | 138 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1750.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1138.8136 | 152.18 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.5 | 138 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 40.87 | 122.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.15 | 61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417 | 90 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 575 | 100 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860.1666 | 65 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4048.75 | 75 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72456 | 120 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3900 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 28475.5333 | 23 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 390 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 540 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 8786 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1045.9999 | 120 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3127.5 | 139 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4430.1833 | 127 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 33.044 | 82.61 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 615 | 41 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 13579.4766 | 85.72 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7283.8 | 12 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 299.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 88.8333 | 130 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 449523.4333 | 154 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2955.1666 | 70 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 2.08 | 7.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 113.9166 | 136.7 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 153.5733 | 44.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 173.25 | 59.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 98.3066 | 58.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 217.765 | 44.9 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 24 | 1 | 1 | 2 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 145.9466 | 42.1 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 198 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 236.4266 | 40.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 273.5833 | 49 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 72 | 3 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 144 | 6 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 2005.15 | 17 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1257.3 | 54 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 83.512 | 11.68 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 101.8967 | 15.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 100.2466 | 136.7 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 152.005 | 30.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 183.6 | 45.9 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 194.12 | 55.2 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 247.52 | 54.6 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 258.44 | 42.6 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 284.745 | 46.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 308.9266 | 62.2 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 380.25 | 58.5 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 214.2667 | 2 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 45 | 10 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 170.1233 | 32.2 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 751.3333 | 49 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 113.905 | 32.7 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 186.9067 | 34.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 2515.05 | 23 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 36.6 | 48.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 192 | 4 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 986.19 | 21.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 650-Fluidized Bed
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 297.9332 | 218 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 800-Miscellaneous
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 18603.5 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 48.5333 | 32 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 126.9 | 27 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 4061.8333 | 2 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 1194.05 | 33 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 46.8166 | 53 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 35.75 | 33 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 1155.2 | 32 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 26.6667 | 20 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 86 | 15 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 58830.933 | 506 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 89.6 | 112 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 10856.1267 | 45.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 507.3328 | 761 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3368.7766 | 53.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 13171.59 | 55.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 36.8333 | 17 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1088.17 | 103.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 21780.19 | 45.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1386.893 | 483.8 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1658.5 | 31 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1674 | 31 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 41.25 | 55 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 270.5416 | 64.93 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 241.4 | 71 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Summer | 39 | 52 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 259.826 | 185.59 | 1 | 1 | 3210-Circulating water pumps | SF-Startup Failure | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 204.149 | 185.59 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 805.4498 | 267 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 7014.6 | 162 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 173.55 | 267 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 525.0998 | 267 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 160.8445 | 185.59 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 821.0832 | 167 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 206.6938 | 64.93 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Winter | 765.4166 | 167 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 18637.29 | 79.8 | 2 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 200.25 | 267 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3081.6666 | 43 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 160.3 | 229 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 23560.6 | 28 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 545.9999 | 90 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2700 | 50 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 43932.8666 | 82 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 58.8266 | 110.3 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 3220.0833 | 85 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 16652.115 | 71.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 485.3331 | 416 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 430.005 | 98.1 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 618.6667 | 20 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 33 | 44 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 1046.9331 | 416 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1970.3 | 323 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 534.75 | 93 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.0566 | 109.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.8666 | 49 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.7999 | 194.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.64 | 179.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1876.8 | 144 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6224.8332 | 170 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2891.6667 | 50 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 231.4666 | 248 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2261.9999 | 180 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.0132 | 154.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.0332 | 158 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1013.5999 | 168 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 170.333 | 28.87 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 11367.1833 | 31 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 30498.65 | 39 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.0667 | 41 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 394 | 60 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 723.7333 | 92 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2016.07 | 69.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11001 | 193 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17214.1 | 158 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 233.3332 | 200 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6509.0667 | 11 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 197.035 | 75.3 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28437.5 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 45988.5 | 31 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1273.0664 | 352 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5740.4166 | 115 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14880 | 20 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14852.25 | 205 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 24931.8166 | 269 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 254.2883 | 56.3 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 453.3332 | 170 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18091.6665 | 250 | 1 | 1 | 3211-Circulating water pump motors | D3-Forced - Postponed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1200 | 200 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1507.3332 | 170 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3467.6866 | 69.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.3165 | 301 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 447.8832 | 349 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3009.1666 | 230 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23450 | 200 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 167.9999 | 180 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 8223.25 | 37 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15890 | 280 | 1 | 1 | 3211-Circulating water pump motors | D2-Forced - Delayed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1077.3 | 38 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11251.2 | 144 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4215.3 | 9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150 | 150 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 242.1 | 9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6449.3332 | 280 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 389.7333 | 74 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3889.6 | 286 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1184.3332 | 170 | 1 | 1 | 3211-Circulating water pump motors | D3-Forced - Postponed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32682.5 | 170 | 1 | 1 | 3211-Circulating water pump motors | D3-Forced - Postponed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9987.3 | 243 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.75 | 25 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112.1966 | 69.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 264.465 | 65.3 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 300.3 | 66 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 326.6666 | 70 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 6304.9555 | 11.91 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 27762.1 | 227 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 13659.84 | 189.72 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Summer | 16726.68 | 129.33 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 61651.827 | 160.74 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 15124.2 | 364 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 4667.25 | 122.5 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 12749.0583 | 83.5 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 8869.6916 | 141.5 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 17335.809 | 160.74 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1036.15 | 53 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 650-Fluidized Bed
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 2730.1 | 138 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 650-Fluidized Bed
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 82.03 | 63.1 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 800-Miscellaneous
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 810 | 20 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 336.6667 | 20 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 73.75 | 3 | 1 | 1 | 3211-Circulating water pump motors | D2-Forced - Delayed | 830-Geothermal
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 49.1667 | 2 | 1 | 1 | 3211-Circulating water pump motors | D2-Forced - Delayed | 830-Geothermal
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 611.1666 | 95 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 11831.6665 | 620 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3921.5 | 310 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2424.4666 | 82 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 16.1967 | 22.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 351.4 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 6585.3 | 162 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 14.7633 | 20.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 47.6 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 279.93 | 43.4 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 52.15 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 54.25 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 294.12 | 45.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 346.85 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5574.6 | 38 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 121.9332 | 236 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 7.15 | 6.5 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 233.835 | 35.7 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 737.1 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3016.3 | 21 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 1418.0833 | 77 | 4 | 4 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 7.26 | 6.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 43.0667 | 19 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 722.2 | 69 | 3 | 3 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 19.4367 | 23.8 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 220.08 | 33.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 21.1516 | 25.9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 390 | 120 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 4827.8 | 239 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 47.6 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 52.15 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 240.385 | 36.7 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 303.15 | 47 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 347.2166 | 251 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 351.4 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 74 | 60 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 344.5 | 106 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 61173.5666 | 121 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4694.4 | 32 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Winter | 4567.3332 | 248 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | SERC | Winter | 638.4666 | 61 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 7.59 | 6.9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 5419.75 | 133 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 16.34 | 22.8 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3016.3 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 21.4783 | 26.3 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 54.25 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 346.85 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 712.3666 | 43 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 737.1 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 253.5833 | 17 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 90 | 30 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 153.3333 | 20 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 135.8 | 42 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 499.2 | 166.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 563.3333 | 130 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 864.9 | 31 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 768.2132 | 166.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4197.6 | 466.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9649.6 | 111 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38145.5 | 535 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3407.5 | 290 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5666.2664 | 728 | 1 | 1 | 3220-Circulating water piping | SF-Startup Failure | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 14274.6665 | 530 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16495.6499 | 243 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 12575.25 | 243 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24132.6164 | 427 | 1 | 1 | 3220-Circulating water piping | U2-Forced - Delayed | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 58.3333 | 20 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 193.6667 | 35 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 301.4 | 33 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42530.5832 | 415 | 1 | 1 | 3220-Circulating water piping | U2-Forced - Delayed | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1084.0666 | 92 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2329.6 | 42 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3026.4 | 116.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2856.9333 | 56 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 173 | 30 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 264.0667 | 17 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2136.1599 | 101.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49590.45 | 637 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12746.2 | 202 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 525 | 90 | 1 | 1 | 3220-Circulating water piping | SF-Startup Failure | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3003.2332 | 427 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31892.5332 | 164 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2986.1999 | 162 | 1 | 1 | 3220-Circulating water piping | U2-Forced - Delayed | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6102.7999 | 219 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 388.2666 | 166.4 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1742.85 | 27 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8895.8332 | 427 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29183.2164 | 839 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13709.75 | 61 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 264368.4999 | 213 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 800-Miscellaneous
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 7056.0666 | 106 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 865.6666 | 106 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 2154.5 | 31 | 1 | 1 | 3221-Circulating water piping fouling | U1-Forced - Immediate | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 25443.8333 | 113 | 1 | 1 | 3221-Circulating water piping fouling | D2-Forced - Delayed | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18515.6 | 164 | 1 | 1 | 3221-Circulating water piping fouling | U1-Forced - Immediate | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28962.4164 | 367 | 1 | 1 | 3221-Circulating water piping fouling | D1-Forced - Immediate | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 294 | 294 | 1 | 1 | 3221-Circulating water piping fouling | D1-Forced - Immediate | 850-Combined Cycle Block
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | OG | 852 | CC steam units | SERC | Summer | 280.5 | 17 | 1 | 1 | 3221-Circulating water piping fouling | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255.15 | 63 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 499.5833 | 55 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 613.3333 | 80 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 633.3333 | 80 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 193.8326 | 51.46 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 826.5 | 87 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1480.72 | 26.76 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 44.7 | 44.7 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.5 | 39 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.3333 | 40 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182.0333 | 43 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1306.25 | 275 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 60 | 60 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.425 | 20.55 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124 | 40 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.8333 | 70 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.5833 | 65 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 641.3333 | 74 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.3333 | 50 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2256 | 94 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 160.9333 | 68 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 208 | 52 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 489.1667 | 50 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 644.8333 | 53 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1831.6666 | 70 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 20436.65 | 299 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 73674.0667 | 47 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 552.79 | 44.7 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 226.5 | 151 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 80 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198 | 36 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 246.6666 | 80 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 474 | 60 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 747 | 415 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 214.5 | 130 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2397 | 60 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3782.5 | 85 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7725 | 75 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 864.9 | 279 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 48.425 | 44.7 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152 | 80 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 701.4166 | 95 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 816 | 48 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 841.6667 | 50 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1375 | 55 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14400 | 200 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 849.7905 | 260.14 | 1 | 1 | 3230-Circulating water valves | D2-Forced - Delayed | 200-Nuclear
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 468 | 117 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 850-Combined Cycle Block
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 456 | 114 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 850-Combined Cycle Block
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 555.8999 | 153 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3078.0832 | 215 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 167 | 167 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2967 | 215 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 128.25 | 171 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 1339.4498 | 267 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 20025 | 267 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 159.75 | 213 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 2620.8 | 416 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 516.0332 | 137 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 4180.7998 | 234 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 852-CC steam units
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13714.5 | 30 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27282.1797 | 493.2 | 1 | 1 | 3231-Waterbox | SF-Startup Failure | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0 | 0 | 1 | 1 | 3231-Waterbox | D2-Forced - Delayed | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 51.6 | 36 | 1 | 1 | 3231-Waterbox | D2-Forced - Delayed | 830-Geothermal
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 30.75 | 41 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 830-Geothermal
3231 | Waterbox | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 32278.7498 | 525 | 1 | 1 | 3231-Waterbox | U1-Forced - Immediate | 850-Combined Cycle Block
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 758.4664 | 367 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.2832 | 343 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4093.3665 | 371 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 891.7666 | 31 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | U1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 481.2499 | 375 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1174.9999 | 375 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 342.1998 | 354 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 588.8832 | 397 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.4499 | 327 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 360.5664 | 373 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3114.1164 | 379 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1333.1997 | 396 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 489.7998 | 372 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1942.4999 | 225 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 383.3665 | 371 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1587.1999 | 384 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 343.1664 | 355 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2697.6999 | 318 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2706.2164 | 397 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225.9998 | 339 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.9 | 347 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.7999 | 354 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.3332 | 364 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.9332 | 337 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D3-Forced - Postponed | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1799.4998 | 366 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D3-Forced - Postponed | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 93.8833 | 43 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 800-Miscellaneous
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 51.2 | 32 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 800-Miscellaneous
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 81.4667 | 47 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 800-Miscellaneous
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 627.2 | 49 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 800-Miscellaneous
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 900.9999 | 159 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 852-CC steam units
3233 | Circulating water priming system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8201 | 590 | 1 | 1 | 3233-Circulating water priming system | D1-Forced - Immediate | 100-Fossil-Steam
3233 | Circulating water priming system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7500 | 600 | 1 | 1 | 3233-Circulating water priming system | D1-Forced - Immediate | 100-Fossil-Steam
3233 | Circulating water priming system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6745.8566 | 245.9 | 1 | 1 | 3233-Circulating water priming system | D1-Forced - Immediate | 100-Fossil-Steam
3233 | Circulating water priming system | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 139.5666 | 79 | 1 | 1 | 3233-Circulating water priming system | U1-Forced - Immediate | 800-Miscellaneous
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5409.2999 | 171 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1668.5 | 94 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 48.3333 | 10 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 200-Nuclear
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 31.75 | 12.7 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 200-Nuclear
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 76305.7332 | 130.4 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 200-Nuclear
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 635.4566 | 50.3 | 1 | 1 | 3235-Cooling tower booster pump | U1-Forced - Immediate | 800-Miscellaneous
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.1667 | 10 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 246.7832 | 221 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7039.6666 | 49 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 23641.6 | 64 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 95.5833 | 31 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12937.5 | 54 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1116 | 310 | 1 | 1 | 3238-Cooling tower fan motors | U1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 192 | 64 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.1667 | 50 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 100-Fossil-Steam
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 134.55 | 8.97 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 650-Fluidized Bed
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 317.35 | 11 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 850-Combined Cycle Block
3238 | Cooling tower fan motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 12 | 4 | 1 | 1 | 3238-Cooling tower fan motors | D1-Forced - Immediate | 852-CC steam units
3239 | Cooling tower fan motors - variable speed | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1125.6 | 36 | 1 | 1 | 3239-Cooling tower fan motors - variable speed | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.5 | 102 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 299 | 39 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.3 | 46 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.4833 | 41 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3679.2 | 73 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 233.3333 | 175 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.6666 | 160 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 557.3666 | 46 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.1767 | 7.1 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1793.4 | 122 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2719.2 | 24 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1200.6 | 174 | 1 | 1 | 3240-Cooling tower fans | D3-Forced - Postponed | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Off-Peak | 555.6 | 36 | 1 | 1 | 3240-Cooling tower fans | U1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.324 | 12.28 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.5 | 41 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 584.25 | 57 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 265.2 | 52 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149489.4998 | 258 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 260.4166 | 125 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 317.4999 | 150 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5838.2499 | 363 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 820 | 410 | 1 | 1 | 3240-Cooling tower fans | U1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1007.5 | 130 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1063.129 | 81.57 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1606.5 | 102 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 509.5999 | 168 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2461.3332 | 355 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 100-Fossil-Steam
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | MRO | Summer | 1129.9033 | 83.8 | 1 | 1 | 3240-Cooling tower fans | D2-Forced - Delayed | 200-Nuclear
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 942.0042 | 13.87 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 200-Nuclear
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 39 | 3.9 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.6 | 3.4 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 39.6 | 4.4 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 41.8 | 3.8 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 42 | 4.2 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 40.2 | 6.7 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 650-Fluidized Bed
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13.3333 | 10 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 350.2 | 103 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4.9 | 6 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 40 | 10 | 1 | 2 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 12.15 | 9 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 108.4 | 4 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 101.25 | 27 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 22.8333 | 10 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 72.6667 | 10 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 82.1667 | 10 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1.9833 | 17 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 70.5 | 10 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 850-Combined Cycle Block
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 7.5 | 5 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 851-CC GT units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 667 | 46 | 1 | 1 | 3240-Cooling tower fans | U1-Forced - Immediate | 851-CC GT units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 270.6333 | 4.6 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 852-CC steam units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 328.5332 | 176 | 1 | 1 | 3240-Cooling tower fans | U2-Forced - Delayed | 861-CoG GT units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 485.8 | 12 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 862-CoG steam units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 28671.25 | 75 | 1 | 1 | 3240-Cooling tower fans | D1-Forced - Immediate | 862-CoG steam units
3240 | Cooling tower fans | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 183.7173 | 98.42 | 1 | 1 | 3240-Cooling tower fans | D2-Forced - Delayed | 862-CoG steam units
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106.3333 | 10 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 322.7437 | 19.58 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 317 | 60 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1079.2833 | 77 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2027.5 | 50 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2034.1166 | 127 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2085.3333 | 68 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 414.1667 | 50 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 402.3735 | 24.61 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 630 | 70 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 703.7 | 62 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.9167 | 5 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 148.0442 | 14.35 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 251.9473 | 22.63 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.6667 | 10 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.5 | 10 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 325.1445 | 30.53 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 371.875 | 29.75 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1142.1666 | 77 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 166 | 20 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 196.65 | 27 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 253 | 30 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 540 | 50 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1327.6999 | 102 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.0093 | 14.68 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 262.4 | 48 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 948.2666 | 127 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.6667 | 10 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 103.0187 | 8.78 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 327.547 | 27.07 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 340.2117 | 24.1 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3241 | Cooling tower efficiency below design | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 264.3333 | 20 | 1 | 1 | 3241-Cooling tower efficiency below design | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 494.6833 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.2833 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 684.5166 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 592.25 | 20.6 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1063.0666 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1096.5666 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15680.25 | 10.1 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 559.45 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 734.7666 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 769.3833 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1224.9833 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 351.75 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 569.5 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 588.4833 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 629.8 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 719.1333 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1032.9166 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1041.85 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50542.2666 | 67.6 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.3833 | 14.6 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3756.4666 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3242 | Cooling tower fill damage | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 960.3333 | 67 | 1 | 1 | 3242-Cooling tower fill damage | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 998.5 | 30 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32021.5332 | 268 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 404688.8 | 188 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 21.8342 | 1.97 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6667 | 32 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 780.1 | 107.6 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17289.5666 | 221 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 778.4331 | 386 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 31.823 | 2.42 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11265.5 | 30 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.5 | 10 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 270 | 30 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 532.5 | 150 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11186 | 238 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 202673.5166 | 61 | 1 | 1 | 3245-Other cooling tower problems | U1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15568 | 278 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 362.1 | 213 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 71571.1866 | 53.6 | 1 | 1 | 3245-Other cooling tower problems | U1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15354.9665 | 238 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9965.3331 | 404 | 1 | 1 | 3245-Other cooling tower problems | U1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 652 | 30 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1011.1667 | 10 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 738.0998 | 366 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 367.2 | 216 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.75 | 15 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 22504 | 116 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32786 | 169 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 100-Fossil-Steam
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 52.5 | 9 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 96 | 20 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 101.65 | 19 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 30.9 | 6 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 59.0333 | 11 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 69.3 | 9 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 84.6667 | 20 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 169.25 | 15 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 28 | 14 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 31.35 | 9 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 63.25 | 15 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 660.8333 | 26 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 56.55 | 13 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 96.8 | 11 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 152.6 | 14 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 542.9333 | 16 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 30.1333 | 16 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 95.3333 | 10 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 23.2 | 12 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 151.25 | 25 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 119 | 17 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 218.25 | 27 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 200-Nuclear
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 10366.4 | 16 | 1 | 1 | 3245-Other cooling tower problems | D2-Forced - Delayed | 830-Geothermal
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 38 | 38 | 1 | 1 | 3245-Other cooling tower problems | U1-Forced - Immediate | 850-Combined Cycle Block
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 164.6999 | 162 | 1 | 1 | 3245-Other cooling tower problems | U1-Forced - Immediate | 851-CC GT units
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Winter | 177.9166 | 175 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 852-CC steam units
3245 | Other cooling tower problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 36374.3333 | 28 | 1 | 1 | 3245-Other cooling tower problems | D1-Forced - Immediate | 862-CoG steam units
3246 | Cooling tower fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19887.0833 | 55 | 1 | 1 | 3246-Cooling tower fouling | D1-Forced - Immediate | 100-Fossil-Steam
3246 | Cooling tower fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2262.5 | 50 | 1 | 1 | 3246-Cooling tower fouling | D1-Forced - Immediate | 100-Fossil-Steam
3246 | Cooling tower fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 105 | 21 | 2 | 2 | 3246-Cooling tower fouling | D1-Forced - Immediate | 851-CC GT units
3246 | Cooling tower fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 100 | 20 | 1 | 1 | 3246-Cooling tower fouling | D1-Forced - Immediate | 852-CC steam units
3247 | Cooling tower instrumentation | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 492.2665 | 208 | 1 | 1 | 3247-Cooling tower instrumentation | U1-Forced - Immediate | 851-CC GT units
3247 | Cooling tower instrumentation | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 140.3999 | 162 | 2 | 2 | 3247-Cooling tower instrumentation | U1-Forced - Immediate | 851-CC GT units
3247 | Cooling tower instrumentation | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 398.6665 | 208 | 1 | 1 | 3247-Cooling tower instrumentation | U1-Forced - Immediate | 851-CC GT units
3247 | Cooling tower instrumentation | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 425.8832 | 253 | 1 | 1 | 3247-Cooling tower instrumentation | U1-Forced - Immediate | 852-CC steam units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 113.4 | 21 | 1 | 1 | 3250-Circulating water system instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1131.4498 | 357.3 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 850-Combined Cycle Block
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 871 | 335 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 851-CC GT units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 2358.2882 | 211.19 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 851-CC GT units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 753.2442 | 211.19 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 851-CC GT units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 1211.5831 | 335 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 851-CC GT units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 4618.0212 | 211.19 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 851-CC GT units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 5071.125 | 405.69 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 852-CC steam units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 72.6915 | 207.69 | 1 | 1 | 3250-Circulating water system instruments and controls | D1-Forced - Immediate | 852-CC steam units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 955.374 | 207.69 | 1 | 1 | 3250-Circulating water system instruments and controls | D1-Forced - Immediate | 852-CC steam units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1246.6664 | 400 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 852-CC steam units
3250 | Circulating water system instruments and controls | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1791.7972 | 405.69 | 1 | 1 | 3250-Circulating water system instruments and controls | U1-Forced - Immediate | 852-CC steam units
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 910.6667 | 20 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 275 | 220 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 329.3333 | 130 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 18683.3332 | 200 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 13384.1082 | 176.3 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25359.3663 | 502 | 1 | 1 | 3260-Traveling screens | U1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78 | 52 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.6666 | 110 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7325.9999 | 270 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4436.6666 | 110 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12947.4 | 108 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3871.6666 | 230 | 1 | 1 | 3260-Traveling screens | U1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259.1667 | 50 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 699.3 | 222 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 158 | 158 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 300.9999 | 210 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 427.1666 | 110 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8680 | 112 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 56783.67 | 376.3 | 1 | 1 | 3260-Traveling screens | U1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5343.6666 | 170 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4381.9999 | 120 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 100 | 120 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 199.3332 | 230 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2894.0332 | 158 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 47276.3749 | 169.5 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3260 | Traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | TRE | Summer | 94.9833 | 139 | 1 | 1 | 3260-Traveling screens | D1-Forced - Immediate | 852-CC steam units
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 60 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446 | 60 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1827 | 210 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.5 | 90 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1260 | 105 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361.23 | 120.41 | 2 | 2 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1060.88 | 132.61 | 2 | 2 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1732.5 | 75 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 52 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199 | 60 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2114 | 151 | 1 | 1 | 3261-Traveling screen fouling | U2-Forced - Delayed | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1206 | 90 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 586.68 | 48.89 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.7999 | 147 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176 | 110 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5332.5 | 45 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 100-Fossil-Steam
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 31.23 | 34.7 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 200-Nuclear
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 47.4583 | 42.5 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 200-Nuclear
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 15.12 | 32.4 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 200-Nuclear
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0 | 0 | 1 | 1 | 3261-Traveling screen fouling | D3-Forced - Postponed | 200-Nuclear
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 12.2667 | 23 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 200-Nuclear
3261 | Traveling screen fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 22.22 | 40.4 | 1 | 1 | 3261-Traveling screen fouling | D1-Forced - Immediate | 200-Nuclear
3269 | Circulating water biological conditions (ie; zebra mussels) | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 253.8166 | 157 | 1 | 1 | 3269-Circulating water biological conditions (ie; zebra mussels) | U1-Forced - Immediate | 800-Miscellaneous
3269 | Circulating water biological conditions (ie; zebra mussels) | NULL | NULL | U1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Summer | 413.4333 | 157 | 1 | 1 | 3269-Circulating water biological conditions (ie; zebra mussels) | U1-Forced - Immediate | 800-Miscellaneous
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 296 | 37 | 1 | 1 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 317.9999 | 180 | 1 | 1 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 100-Fossil-Steam
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1032.7333 | 28 | 1 | 1 | 3270-Intake system problems other than traveling screens | D2-Forced - Delayed | 100-Fossil-Steam
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1592.85 | 63 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 100-Fossil-Steam
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 27148.3333 | 52 | 1 | 1 | 3270-Intake system problems other than traveling screens | U3-Forced - Postponed | 100-Fossil-Steam
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7542.3332 | 242 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 12494.2498 | 243 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 10373.3331 | 320 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 11785.2 | 322 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 25612.7665 | 587 | 1 | 1 | 3270-Intake system problems other than traveling screens | D2-Forced - Delayed | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 8194 | 241 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 114874.1997 | 972 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 8377.2332 | 242 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 850-Combined Cycle Block
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 413.6 | 47 | 1 | 1 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 851-CC GT units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1773.5666 | 77 | 1 | 1 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 851-CC GT units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 10386.25 | 175 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 851-CC GT units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 677.6 | 77 | 2 | 2 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 851-CC GT units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 10380.4165 | 175 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 851-CC GT units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Summer | 9232.5 | 150 | 1 | 1 | 3270-Intake system problems other than traveling screens | U1-Forced - Immediate | 852-CC steam units
3270 | Intake system problems other than traveling screens | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1161.6 | 132 | 2 | 2 | 3270-Intake system problems other than traveling screens | D1-Forced - Immediate | 852-CC steam units
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1210 | 220 | 1 | 1 | 3271-Intake grating fouling | U1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.25 | 35 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 571.6667 | 35 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 224.75 | 31 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.5 | 30 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.3333 | 40 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154 | 28 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 100-Fossil-Steam
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 55 | 15 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 800-Miscellaneous
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 403.6 | 12 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 800-Miscellaneous
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 418.625 | 334.9 | 1 | 1 | 3271-Intake grating fouling | U1-Forced - Immediate | 850-Combined Cycle Block
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 1550.9166 | 185 | 2 | 2 | 3271-Intake grating fouling | U1-Forced - Immediate | 851-CC GT units
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 1757.5 | 185 | 2 | 2 | 3271-Intake grating fouling | U1-Forced - Immediate | 851-CC GT units
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 392.4666 | 58 | 1 | 1 | 3271-Intake grating fouling | D1-Forced - Immediate | 852-CC steam units
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 1978.4666 | 236 | 1 | 1 | 3271-Intake grating fouling | U1-Forced - Immediate | 852-CC steam units
3271 | Intake grating fouling | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Winter | 2596 | 236 | 1 | 1 | 3271-Intake grating fouling | U1-Forced - Immediate | 852-CC steam units
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 113.1 | 377 | 1 | 1 | 3272-Circulating water screenwash system | D1-Forced - Immediate | 100-Fossil-Steam
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3188.8164 | 653 | 1 | 1 | 3272-Circulating water screenwash system | D1-Forced - Immediate | 100-Fossil-Steam
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 685210.0665 | 377 | 1 | 1 | 3272-Circulating water screenwash system | D1-Forced - Immediate | 100-Fossil-Steam
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 13862.4998 | 375 | 1 | 1 | 3272-Circulating water screenwash system | D1-Forced - Immediate | 100-Fossil-Steam
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.9333 | 82 | 1 | 1 | 3272-Circulating water screenwash system | D2-Forced - Delayed | 100-Fossil-Steam
3272 | Circulating water screenwash system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1763.9997 | 378 | 1 | 1 | 3272-Circulating water screenwash system | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 471.5 | 41 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16975.2 | 308.64 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | U1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 79.9 | 94 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1666.994 | 153.64 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 32.6333 | 89 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 84.5833 | 145 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 100-Fossil-Steam
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 5865.8 | 278 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 200-Nuclear
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 6.5633 | 1.1 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 200-Nuclear
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 890.1 | 27 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 200-Nuclear
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 111.24 | 21.6 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 200-Nuclear
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Off-Peak | 359.4593 | 54.74 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 800-Miscellaneous
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Winter | 120.988 | 62.58 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 800-Miscellaneous
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Winter | 154.665 | 49.1 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 800-Miscellaneous
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Winter | 183.144 | 52.83 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 800-Miscellaneous
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 800 | Miscellaneous | NPCC | Winter | 152.4418 | 52.87 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 800-Miscellaneous
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 919.479 | 151.98 | 2 | 2 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 851-CC GT units
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 569.6319 | 152.58 | 2 | 2 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 851-CC GT units
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 633.7333 | 169.75 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 852-CC steam units
3273 | Debris in circulating water from outside sources (leaves; mud; etc.) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 1027.5925 | 169.85 | 1 | 1 | 3273-Debris in circulating water from outside sources (leaves; mud; etc.) | D1-Forced - Immediate | 852-CC steam units
3274 | Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1833.333 | 440 | 1 | 1 | 3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | D1-Forced - Immediate | 100-Fossil-Steam
3274 | Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61789.5 | 690 | 1 | 1 | 3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | U1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1 | 39 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 980.5 | 31.8 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3269.9 | 114 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 453.4333 | 223 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.7166 | 77 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 437.7666 | 46 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.6666 | 28 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.4 | 22 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.5167 | 23 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1119.25 | 36.3 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 411.6667 | 50 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.75 | 25 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.25 | 21 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 592.1666 | 323 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5702.4 | 32.4 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.0333 | 38 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172 | 43 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260 | 100 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 7922.5 | 75 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11278.3416 | 133.34 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.4 | 76 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8667 | 16 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135.1166 | 121 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 369.8666 | 152 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 100-Fossil-Steam
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1008 | 7 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 2184 | 7 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3744 | 12 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 383.9333 | 4 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1572.5 | 17 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 144 | 6 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 600 | 5 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 9688 | 28 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 6538.56 | 11.12 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 192 | 4 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 603.1667 | 7 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 13698.94 | 9.37 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 24 | 1 | 1 | 3 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 631.25 | 5 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 96 | 2 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1320 | 11 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 2828 | 14 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 72 | 3 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 168 | 7 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 480 | 5 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 9120 | 38 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 25542.4547 | 11.12 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 576 | 8 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1728 | 24 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3696 | 14 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 200-Nuclear
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 94 | 4.7 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 650-Fluidized Bed
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 44.2 | 3.4 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 650-Fluidized Bed
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 93.6 | 3.6 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 650-Fluidized Bed
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1156.1333 | 232 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 515.6666 | 260 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1536.3333 | 220 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 279.65 | 141 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D2-Forced - Delayed | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 303.4499 | 153 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D2-Forced - Delayed | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 147.3332 | 260 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 876.3333 | 220 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D2-Forced - Delayed | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1360 | 272 | 1 | 3 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 436.3333 | 220 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1300 | 260 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1300 | 260 | 1 | 2 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D3-Forced - Postponed | 850-Combined Cycle Block
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 49.6667 | 20 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 852-CC steam units
3280 | High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 107.8 | 14 | 1 | 1 | 3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | D1-Forced - Immediate | 852-CC steam units
3281 | Circulating water tempering system | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3847.4999 | 243 | 1 | 1 | 3281-Circulating water tempering system | SF-Startup Failure | 100-Fossil-Steam
3281 | Circulating water tempering system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 995.3667 | 6.5 | 2 | 2 | 3281-Circulating water tempering system | D1-Forced - Immediate | 851-CC GT units
3281 | Circulating water tempering system | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 624 | 48 | 1 | 1 | 3281-Circulating water tempering system | D1-Forced - Immediate | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6124.5 | 90 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 100-Fossil-Steam
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 362.4332 | 262 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 100-Fossil-Steam
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 558.3333 | 50 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 100-Fossil-Steam
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 676.6666 | 140 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 100-Fossil-Steam
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 548.2666 | 128 | 2 | 2 | 3285-Circulating water chemistry | D1-Forced - Immediate | 100-Fossil-Steam
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2029.45 | 111 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 851-CC GT units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 5667.75 | 229 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 851-CC GT units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 5884.8499 | 111 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 851-CC GT units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 6324.2165 | 229 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 851-CC GT units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 49 | 49 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1726.45 | 73 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 0 | 0 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 26 | 26 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 355 | 71 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 294 | 42 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 448.7333 | 53 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2595.4 | 76 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 210 | 70 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 15099.3333 | 116 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 65.1083 | 150.25 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1304 | 163 | 1 | 2 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 148 | 148 | 1 | 2 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 153 | 153 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 8173.6 | 300.5 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1888 | 118 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 86 | 43 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 608.3166 | 113 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1092 | 156 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 5149.9166 | 145 | 1 | 1 | 3285-Circulating water chemistry | U1-Forced - Immediate | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3419.575 | 64.5 | 1 | 1 | 3285-Circulating water chemistry | D1-Forced - Immediate | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 857.4666 | 118 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 160 | 20 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1141 | 163 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1695 | 113 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 978 | 163 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 10896.9666 | 113 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1332 | 148 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3285 | Circulating water chemistry | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 50 | 50 | 1 | 1 | 3285-Circulating water chemistry | D2-Forced - Delayed | 852-CC steam units
3292 | Waste water (zero discharge) piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 499.4833 | 23 | 1 | 1 | 3292-Waste water (zero discharge) piping | U1-Forced - Immediate | 100-Fossil-Steam
3295 | Other Waste water (zero discharge) problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 168 | 21 | 1 | 9 | 3295-Other Waste water (zero discharge) problems | D1-Forced - Immediate | 100-Fossil-Steam
3295 | Other Waste water (zero discharge) problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 120 | 15 | 3 | 27 | 3295-Other Waste water (zero discharge) problems | D1-Forced - Immediate | 100-Fossil-Steam
3295 | Other Waste water (zero discharge) problems | NULL | NULL | D1 | Forced - Immediate | 2020 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Summer | 120 | 15 | 8 | 72 | 3295-Other Waste water (zero discharge) problems | D1-Forced - Immediate | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
3295 | Other Waste water (zero discharge) problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 42.25 | 13 | 2 | 2 | 3295-Other Waste water (zero discharge) problems | D1-Forced - Immediate | 860-Co-generator Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.5 | 18 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 653.4 | 59.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1400.8 | 54.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9880 | 190 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1224.5 | 158 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1557 | 173 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 198.3333 | 17 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1670.2333 | 178 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1958 | 178 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 644 | 64.4 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1413.6 | 74.4 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2210.5999 | 84 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9773.3328 | 800 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 19494.5666 | 158 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.2 | 64.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1246 | 178 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2016 | 168 | 2 | 2 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2147.5999 | 168 | 2 | 2 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4564.6665 | 410 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.28 | 69.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1677.6666 | 70 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12112.8 | 98 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2204.9333 | 184 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 634.5 | 18 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1369.5832 | 173 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.1667 | 10 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1643.5 | 173 | 2 | 4 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4.15 | 83 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1211 | 173 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1424 | 178 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1770.6666 | 83 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2016 | 168 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1246 | 178 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1146.42 | 59.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3811.2 | 79.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5628 | 168 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2270.1 | 64.4 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 993.9999 | 168 | 2 | 2 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1677.1999 | 168 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90393.3328 | 728 | 1 | 1 | 3299-Other circulating water system problems | U2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 179.0667 | 17 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1671.6 | 168 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10039.5 | 690 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1223.6 | 64.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1512 | 168 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.16666 | 10 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.5 | 10 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 337.45 | 79.4 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 493.3333 | 100 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27518.9999 | 180 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2032.75 | 173 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 346 | 173 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1384 | 173 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1602 | 178 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1667.2665 | 178 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2133.0333 | 178 | 2 | 2 | 3299-Other circulating water system problems | D1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 864 | 18 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1428 | 168 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 37184.2666 | 164 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 100-Fossil-Steam
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 876.3 | 138 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 650-Fluidized Bed
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 15.3333 | 10 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 35.4 | 18 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 72.7666 | 118 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 326.3521 | 70.69 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 9.3333 | 5 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 73.3833 | 119 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 29.5 | 5 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 303.2226 | 65.68 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 86.9499 | 141 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 393.8666 | 56 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 124.2 | 46 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1971.9 | 126 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 2263.2499 | 165 | 2 | 2 | 3299-Other circulating water system problems | U1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 208.9166 | 115 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 230.7166 | 127 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 12160.3832 | 167 | 1 | 1 | 3299-Other circulating water system problems | U2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1698.75 | 225 | 1 | 1 | 3299-Other circulating water system problems | U3-Forced - Postponed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 414.9666 | 59 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 325.2666 | 119 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 436.0666 | 62 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 443.1 | 63 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 118.8 | 44 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 513.6833 | 119 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1893.65 | 121 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Gas | GG | 851 | CC GT units | RFC | Summer | 12046.2666 | 167 | 1 | 1 | 3299-Other circulating water system problems | U2-Forced - Delayed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Summer | 5766.3 | 149 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1931.2499 | 225 | 1 | 1 | 3299-Other circulating water system problems | U3-Forced - Postponed | 851-CC GT units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 541.5666 | 77 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4257.4999 | 195 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 120.8083 | 66.5 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3764.5833 | 65 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 258.0666 | 79 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 625.9666 | 89 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1535.8333 | 190 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 212.3333 | 65 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 210.4666 | 77 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 555.6333 | 79 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3461.25 | 65 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 105.3 | 39 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1126.8 | 72 | 1 | 1 | 3299-Other circulating water system problems | D2-Forced - Delayed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4068.9999 | 195 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 250.7999 | 171 | 1 | 1 | 3299-Other circulating water system problems | D3-Forced - Postponed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 16524.0266 | 219.2 | 1 | 1 | 3299-Other circulating water system problems | U2-Forced - Delayed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2139.0665 | 244 | 1 | 1 | 3299-Other circulating water system problems | U3-Forced - Postponed | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 527.5 | 75 | 1 | 1 | 3299-Other circulating water system problems | D1-Forced - Immediate | 852-CC steam units
3299 | Other circulating water system problems | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1920.3332 | 140 | 1 | 1 | 3299-Other circulating water system problems | U1-Forced - Immediate | 852-CC steam units
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4079.5067 | 40.1 | 1 | 1 | 3300-Condensate water pre-treatment | D1-Forced - Immediate | 100-Fossil-Steam
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4251.4999 | 330 | 1 | 1 | 3300-Condensate water pre-treatment | D1-Forced - Immediate | 100-Fossil-Steam
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12274.9333 | 152.8 | 1 | 1 | 3300-Condensate water pre-treatment | U1-Forced - Immediate | 100-Fossil-Steam
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4245.9998 | 330 | 1 | 1 | 3300-Condensate water pre-treatment | D1-Forced - Immediate | 100-Fossil-Steam
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 15352.65 | 98.1 | 1 | 1 | 3300-Condensate water pre-treatment | U1-Forced - Immediate | 850-Combined Cycle Block
3300 | Condensate water pre-treatment | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 66.2667 | 8 | 1 | 1 | 3300-Condensate water pre-treatment | D1-Forced - Immediate | 860-Co-generator Block
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 427.0833 | 205 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1914.25 | 93 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6074.9166 | 269 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 601.9166 | 233 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 3683 | 127 | 1 | 1 | 3310-Condensate/hotwell pumps | D3-Forced - Postponed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 841.4998 | 459 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.524 | 10.26 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1528.3332 | 262 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52681.1999 | 234 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 582.59 | 44.7 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1444 | 60 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4257.3333 | 8 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20664.6833 | 41 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1106.25 | 75 | 1 | 1 | 3310-Condensate/hotwell pumps | D3-Forced - Postponed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 331.25 | 75 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3385.8333 | 85 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13395.2 | 728 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1250.4499 | 267 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1418.9 | 21 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3011.4 | 239 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1120.8 | 9.34 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 31032.55 | 93 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2944.9998 | 465 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 886.6666 | 80 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1926.75 | 21 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259 | 259 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 10866.6666 | 50 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 72049.4665 | 211 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5562.9165 | 395 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 126.1333 | 44 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2111.3333 | 40 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2113.1666 | 155 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 8258.25 | 165 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 208.9999 | 165 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 801.6666 | 65 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1113.75 | 135 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 6580.8 | 54 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2546.0665 | 181 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11997 | 12 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 54962.25 | 95 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1526.4 | 212 | 1 | 1 | 3310-Condensate/hotwell pumps | D3-Forced - Postponed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 319.6333 | 223 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 200 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1149.4166 | 65 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 606.3332 | 170 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 918.8333 | 37 | 2 | 2 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 4534.2 | 108 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3994.6666 | 224 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 260 | 260 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 167.5 | 75 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 175196.9333 | 56 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5981.1666 | 85 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 100-Fossil-Steam
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 49 | 7 | 1 | 1 | 3310-Condensate/hotwell pumps | D3-Forced - Postponed | 200-Nuclear
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 1246.077 | 35.91 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 200-Nuclear
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3576.6666 | 116 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 200-Nuclear
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 98.9626 | 100.64 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 650-Fluidized Bed
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3131.4 | 25.5 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 963.7 | 419 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 654.5 | 42 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 830-Geothermal
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 302.25 | 39 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 830-Geothermal
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 761.8 | 39 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 830-Geothermal
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 1668.55 | 39 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 830-Geothermal
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 340.0832 | 265 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2719.1583 | 115.3 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 129.8333 | 190 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 851-CC GT units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1123.1666 | 230 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 851-CC GT units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Summer | 20864.8332 | 230 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 851-CC GT units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 74.4 | 72 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 708 | 120 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 10.5 | 21 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 9755 | 20 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 27.6666 | 83 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 21 | 21 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 337.6 | 32 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 2272.4 | 46 | 1 | 1 | 3310-Condensate/hotwell pumps | D2-Forced - Delayed | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 23.7 | 158 | 1 | 1 | 3310-Condensate/hotwell pumps | U1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | WECC | Summer | 25809.5 | 10 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3310 | Condensate/hotwell pumps | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 72 | 45 | 1 | 1 | 3310-Condensate/hotwell pumps | D1-Forced - Immediate | 852-CC steam units
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7610.39 | 90.78 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 99291.9666 | 259.7 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 158.4 | 132 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 812.7 | 63 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10678.2 | 222 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 466.3633 | 121.66 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 40945.9332 | 206 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 886 | 120 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1605.28 | 401.32 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1344 | 420 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 562.5 | 225 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 152 | 190 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 700 | 200 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.505 | 129.01 | 1 | 1 | 3311-Condensate/hotwell pump motor | D2-Forced - Delayed | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5633.2499 | 315 | 1 | 1 | 3311-Condensate/hotwell pump motor | D2-Forced - Delayed | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2679 | 570 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7700 | 220 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 960.5 | 113 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48205.6929 | 90.78 | 1 | 1 | 3311-Condensate/hotwell pump motor | D2-Forced - Delayed | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16584.8329 | 659 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1957.6896 | 62.78 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167003.4 | 258 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 633.1733 | 169.6 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 260.1665 | 223 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 100-Fossil-Steam
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 7348.25 | 85 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 200-Nuclear
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 957.5 | 383 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 740.3333 | 20 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 830-Geothermal
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 8.4667 | 2 | 1 | 1 | 3311-Condensate/hotwell pump motor | D2-Forced - Delayed | 830-Geothermal
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 223.4667 | 2 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 830-Geothermal
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 198.9 | 39 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 830-Geothermal
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 622.1165 | 229 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 850-Combined Cycle Block
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 312.65 | 37 | 1 | 1 | 3311-Condensate/hotwell pump motor | D1-Forced - Immediate | 850-Combined Cycle Block
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 164.45 | 299 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 850-Combined Cycle Block
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 330 | 300 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 850-Combined Cycle Block
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 286.65 | 147 | 2 | 2 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 851-CC GT units
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 441 | 147 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 851-CC GT units
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 507 | 260 | 1 | 1 | 3311-Condensate/hotwell pump motor | U1-Forced - Immediate | 852-CC steam units
3311 | Condensate/hotwell pump motor | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 390 | 130 | 1 | 1 | 3311-Condensate/hotwell pump motor | D2-Forced - Delayed | 852-CC steam units
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.3333 | 10 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 356.883 | 437 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3373.6664 | 349 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2809.7999 | 378 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336 | 280 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 22200 | 296 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 200-Nuclear
3312 | Condensate booster pump | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 146.6833 | 13 | 1 | 1 | 3312-Condensate booster pump | D3-Forced - Postponed | 200-Nuclear
3312 | Condensate booster pump | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 132 | 16 | 1 | 1 | 3312-Condensate booster pump | D2-Forced - Delayed | 200-Nuclear
3312 | Condensate booster pump | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5478.3329 | 692 | 1 | 1 | 3312-Condensate booster pump | U1-Forced - Immediate | 850-Combined Cycle Block
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4036.6664 | 346 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 850-Combined Cycle Block
3312 | Condensate booster pump | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 297.9816 | 275.06 | 1 | 1 | 3312-Condensate booster pump | U1-Forced - Immediate | 850-Combined Cycle Block
3312 | Condensate booster pump | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 340.0333 | 202 | 1 | 1 | 3312-Condensate booster pump | U1-Forced - Immediate | 851-CC GT units
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 256.7083 | 152.5 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 852-CC steam units
3312 | Condensate booster pump | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 378 | 18 | 1 | 1 | 3312-Condensate booster pump | D1-Forced - Immediate | 852-CC steam units
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1931.6665 | 380 | 1 | 1 | 3313-Condensate booster pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5004 | 80 | 1 | 1 | 3313-Condensate booster pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1164 | 120 | 1 | 1 | 3313-Condensate booster pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4911.6665 | 350 | 1 | 1 | 3313-Condensate booster pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 448.5 | 78 | 1 | 1 | 3313-Condensate booster pump motor | D1-Forced - Immediate | 100-Fossil-Steam
3313 | Condensate booster pump motor | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1400.0999 | 117 | 1 | 1 | 3313-Condensate booster pump motor | D3-Forced - Postponed | 200-Nuclear
3315 | Condensate booster pump drive (other than 3313 and 3314) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1584.695 | 166.81 | 1 | 1 | 3315-Condensate booster pump drive (other than 3313 and 3314) | D2-Forced - Delayed | 200-Nuclear
3320 | Condensate piping | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1067.5 | 35 | 1 | 1 | 3320-Condensate piping | D1-Forced - Immediate | 100-Fossil-Steam
3320 | Condensate piping | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 850.65 | 159 | 1 | 1 | 3320-Condensate piping | D1-Forced - Immediate | 100-Fossil-Steam
3320 | Condensate piping | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 873.2333 | 17 | 1 | 1 | 3320-Condensate piping | D1-Forced - Immediate | 100-Fossil-Steam
3320 | Condensate piping | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9136.1665 | 410 | 1 | 1 | 3320-Condensate piping | U1-Forced - Immediate | 100-Fossil-Steam
3320 | Condensate piping | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 685.6664 | 340 | 1 | 1 | 3320-Condensate piping | U1-Forced - Immediate | 100-Fossil-Steam
3320 | Condensate piping | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2723.3416 | 95.5 | 1 | 1 | 3320-Condensate piping | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3320 | Condensate piping | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 2923.9998 | 255 | 1 | 1 | 3320-Condensate piping | U1-Forced - Immediate | 850-Combined Cycle Block
3320 | Condensate piping | Balance of Plant | Condensate System | SF | Startup Failure | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2216.7 | 246.3 | 1 | 1 | 3320-Condensate piping | SF-Startup Failure | 850-Combined Cycle Block
3320 | Condensate piping | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2489.2333 | 106 | 1 | 1 | 3320-Condensate piping | U1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 470.25 | 855 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1044.9 | 54 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 836.7916 | 105.7 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 273 | 91 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2637.25 | 55 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14233.3331 | 700 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16397.3328 | 860 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 182.3999 | 144 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3203.0833 | 85 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1024.4667 | 44 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5908.8 | 32 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 44031.2 | 48 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 84222 | 54 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 746.2665 | 193 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1816.4667 | 44 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19724.3828 | 773 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.6664 | 400 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.225 | 80.3 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1933.8666 | 37 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 161.6667 | 25 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 397.5 | 45 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 100-Fossil-Steam
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 75.5332 | 206 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 12.7999 | 384 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 41.6665 | 500 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 57.3332 | 430 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 37.4999 | 450 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 67 | 335 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 29.9999 | 360 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 196.6665 | 590 | 1 | 1 | 3330-Condensate valves | D1-Forced - Immediate | 850-Combined Cycle Block
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 553.0479 | 227.28 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 851-CC GT units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 7836.7999 | 192 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 851-CC GT units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 272.736 | 227.28 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 851-CC GT units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 188.4999 | 174 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 851-CC GT units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 8155.8 | 197 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 851-CC GT units
3330 | Condensate valves | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 131.0833 | 121 | 1 | 1 | 3330-Condensate valves | D2-Forced - Delayed | 852-CC steam units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 10244.9832 | 251 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 852-CC steam units
3330 | Condensate valves | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 839.9875 | 305.45 | 1 | 1 | 3330-Condensate valves | U1-Forced - Immediate | 852-CC steam units
3339 | LP heater head leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 402.975 | 99.5 | 1 | 1 | 3339-LP heater head leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52 | 40 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3323.25 | 63 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38827.9998 | 510 | 1 | 1 | 3340-LP heater tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 765 | 30 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 261.3333 | 196 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.4 | 8 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7370.3166 | 163 | 1 | 1 | 3340-LP heater tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1604.6666 | 40 | 1 | 1 | 3340-LP heater tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8917.5 | 10 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10758 | 30 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.2 | 96 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.6667 | 50 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 287 | 30 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3340 | LP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.5 | 90 | 1 | 1 | 3340-LP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3009.1666 | 157 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 26 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.25 | 45 | 1 | 1 | 3341-Other LP heater - general | D2-Forced - Delayed | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6188 | 34 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36698.6664 | 448 | 1 | 1 | 3341-Other LP heater - general | U1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3930.2333 | 157 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.5833 | 61 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1231.05 | 283 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55.4999 | 90 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1280.6664 | 680 | 1 | 1 | 3341-Other LP heater - general | U1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 59.527 | 93.99 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161 | 21 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3341 | Other LP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4640.6666 | 40 | 1 | 1 | 3341-Other LP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3342 | IP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1733.75 | 365 | 1 | 1 | 3342-IP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3342 | IP heater tube leaks | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2272.05 | 561 | 1 | 1 | 3342-IP heater tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3342 | IP heater tube leaks | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 70630.5328 | 824 | 1 | 1 | 3342-IP heater tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3343 | Other IP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34041.6666 | 50 | 1 | 1 | 3343-Other IP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3343 | Other IP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11038.5833 | 31 | 1 | 1 | 3343-Other IP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3343 | Other IP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3285 | 27 | 1 | 1 | 3343-Other IP heater - general | D1-Forced - Immediate | 100-Fossil-Steam
3343 | Other IP heater - general | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 568.2 | 227.28 | 1 | 1 | 3343-Other IP heater - general | U1-Forced - Immediate | 851-CC GT units
3343 | Other IP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 80.1413 | 117.28 | 1 | 1 | 3343-Other IP heater - general | D1-Forced - Immediate | 851-CC GT units
3343 | Other IP heater - general | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | RFC | Winter | 486.8908 | 152.95 | 1 | 1 | 3343-Other IP heater - general | D1-Forced - Immediate | 852-CC steam units
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1162.7997 | 513 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 12.8333 | 35 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 102.9167 | 5 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 474.5831 | 425 | 1 | 1 | 3344-Deaerator (including level control) | D3-Forced - Postponed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 593 | 12 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 284.1666 | 275 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 431.9166 | 71 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075.6516 | 348.86 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.8333 | 10 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23826.1332 | 448 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 269.8 | 38 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5039.7998 | 339 | 1 | 1 | 3344-Deaerator (including level control) | U2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136000 | 680 | 1 | 1 | 3344-Deaerator (including level control) | U3-Forced - Postponed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.75 | 15 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | SF | Startup Failure | 2020 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 803 | 292 | 1 | 1 | 3344-Deaerator (including level control) | SF-Startup Failure | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5224.9332 | 526 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.3333 | 26 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2949.7832 | 493 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9221.3329 | 1330 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41223 | 455 | 1 | 1 | 3344-Deaerator (including level control) | U2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 63.805 | 127.61 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 37.05 | 39 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15 | 20 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30344.5332 | 448 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3516.7997 | 471 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3807.733 | 524 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 78.5333 | 38 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 53.1 | 59 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 159.3 | 8.85 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8359.11 | 70.9 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2287.4999 | 450 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2665.383 | 443 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1913.7332 | 463 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.9167 | 5 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1656.1665 | 190 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76.1667 | 10 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 139.6667 | 20 | 1 | 1 | 3344-Deaerator (including level control) | D2-Forced - Delayed | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15898.75 | 395 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 31789.3328 | 728 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 780 | 45 | 1 | 1 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 100-Fossil-Steam
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 22.35 | 22.35 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 650-Fluidized Bed
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 819.62 | 30.64 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 650-Fluidized Bed
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 47.22 | 23.61 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 650-Fluidized Bed
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 49 | 35 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 5506.6666 | 160 | 1 | 1 | 3344-Deaerator (including level control) | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U3 | Forced - Postponed | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 71540.1966 | 139.9 | 1 | 1 | 3344-Deaerator (including level control) | U3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1203.445 | 69.9 | 1 | 1 | 3344-Deaerator (including level control) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3344 | Deaerator (including level control) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Summer | 39.5 | 158 | 2 | 2 | 3344-Deaerator (including level control) | U1-Forced - Immediate | 851-CC GT units
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.3333 | 20 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3146.195 | 126.1 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1672.4167 | 35 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2098.25 | 35 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.689 | 25.71 | 1 | 1 | 3350-Condensate polishing and filtering systems | D2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 606 | 120 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 743.75 | 175 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 540.1549 | 75.9 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2223.2816 | 95.9 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 735 | 35 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1140 | 60 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3160.5 | 70 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.9358 | 50.65 | 1 | 1 | 3350-Condensate polishing and filtering systems | D2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31200 | 1300 | 1 | 1 | 3350-Condensate polishing and filtering systems | U1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471.75 | 45 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.6667 | 25 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 300 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4755 | 60 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 69427.6166 | 263 | 1 | 1 | 3350-Condensate polishing and filtering systems | D3-Forced - Postponed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 652.5 | 450 | 1 | 1 | 3350-Condensate polishing and filtering systems | U1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2070.9998 | 570 | 1 | 1 | 3350-Condensate polishing and filtering systems | U1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 139.1 | 78 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 50 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.7028 | 175.63 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650 | 25 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5660 | 75 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1257.45 | 83 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1726.3 | 61 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3061.4999 | 90 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4002.8333 | 70 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.3333 | 20 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.6667 | 50 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4595 | 75 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2789.9996 | 540 | 1 | 1 | 3350-Condensate polishing and filtering systems | D2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 60456.4999 | 213 | 1 | 1 | 3350-Condensate polishing and filtering systems | D3-Forced - Postponed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 159.4667 | 26 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 674.8324 | 426.21 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.7 | 83 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.05 | 69 | 1 | 1 | 3350-Condensate polishing and filtering systems | D2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D3 | Forced - Postponed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 910 | 130 | 1 | 1 | 3350-Condensate polishing and filtering systems | D3-Forced - Postponed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26717.5998 | 546 | 1 | 1 | 3350-Condensate polishing and filtering systems | U2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470.6666 | 40 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3667.3831 | 293 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2210.3331 | 380 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 463.75 | 175 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 770 | 35 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 800.775 | 355.9 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1705.0833 | 35 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3315.4165 | 365 | 1 | 1 | 3350-Condensate polishing and filtering systems | D2-Forced - Delayed | 100-Fossil-Steam
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 91.8 | 17 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 200-Nuclear
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 620.425 | 17.25 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 200-Nuclear
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1118.0847 | 22.28 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 200-Nuclear
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 39.6 | 44 | 1 | 1 | 3350-Condensate polishing and filtering systems | D1-Forced - Immediate | 850-Combined Cycle Block
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 2534 | 181 | 1 | 1 | 3350-Condensate polishing and filtering systems | U1-Forced - Immediate | 851-CC GT units
3350 | Condensate polishing and filtering systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | SERC | Winter | 1429.9 | 181 | 1 | 1 | 3350-Condensate polishing and filtering systems | U1-Forced - Immediate | 851-CC GT units
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 119 | 119 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 254.8333 | 139 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 12868.4 | 424 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 293.0009 | 174.06 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.55 | 39 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3882.3166 | 311 | 1 | 1 | 3351-Chemical addition systems | D1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 270.25 | 115 | 1 | 1 | 3351-Chemical addition systems | D2-Forced - Delayed | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 343.0833 | 115 | 1 | 1 | 3351-Chemical addition systems | D2-Forced - Delayed | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1828.9832 | 427 | 1 | 1 | 3351-Chemical addition systems | U1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4426.5664 | 427 | 1 | 1 | 3351-Chemical addition systems | U1-Forced - Immediate | 100-Fossil-Steam
3351 | Chemical addition systems | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Winter | 7013.1998 | 267 | 1 | 1 | 3351-Chemical addition systems | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 379.9998 | 228 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 738 | 164 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6672.4333 | 94 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8143.75 | 75 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 427.0833 | 125 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 568.7497 | 375 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 243 | 81 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.8833 | 49 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1650 | 150 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 351 | 90 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1513.6 | 344 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1967.25 | 215 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1797.2563 | 49.33 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 627.8833 | 101 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19714.2 | 638 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 65372.2166 | 227 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2171.2082 | 267.5 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3445.1625 | 620.75 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2640.1665 | 217 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 887.9999 | 144 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 328.25 | 101 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 35541.6 | 566.4 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.7 | 127 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 387 | 172 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 496.7083 | 227.5 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5322.9165 | 175 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1803.2667 | 44 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2310 | 231 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7326.0999 | 183 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 127.0833 | 125 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3023.1665 | 187 | 2 | 2 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.3 | 6 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | SF | Startup Failure | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19539.6662 | 730 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | SF-Startup Failure | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U3 | Forced - Postponed | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 31586.8999 | 222 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U3-Forced - Postponed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 534.75 | 93 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1076.4 | 69 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.8 | 24 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2019.0666 | 152 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13524 | 294 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 767.0833 | 175 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 89.3 | 47 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3476.0416 | 177.5 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 89.4667 | 44 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124.2 | 69 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3482.4 | 144 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 305 | 244 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5027.4 | 294 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8869.1832 | 391 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 958.8 | 376 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81.4 | 44 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.25 | 15 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 374 | 44 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 372.1166 | 269 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 35.8333 | 25 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 67.5 | 75 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1999.9999 | 150 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.3333 | 64 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 419.15 | 101 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 50287.1665 | 310 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2004.1 | 147 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 316.4 | 24 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2334.4 | 24 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 504.4 | 194 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 696.6666 | 95 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1524.9997 | 375 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 186 | 31 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D2-Forced - Delayed | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62641 | 740 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 100-Fossil-Steam
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 5630.1814 | 679.7 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 200-Nuclear
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 7411.0703 | 102.41 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 200-Nuclear
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 385 | 42 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 850-Combined Cycle Block
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 8923.2999 | 174 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 3639.1333 | 169 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 4537.5073 | 167.23 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 19215.8999 | 162 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 18775.8 | 162 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9474.3 | 174 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 4554.2303 | 167.23 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | WECC | Winter | 4559.8046 | 167.23 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 9714.9999 | 174 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Winter | 1681.55 | 169 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 851-CC GT units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 398.4 | 96 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 852-CC steam units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 2067.2 | 96 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | D1-Forced - Immediate | 852-CC steam units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 19083.4331 | 362 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 852-CC steam units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 8189.5227 | 301.27 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 852-CC steam units
3352 | Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 18052.5332 | 152 | 1 | 1 | 3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | U1-Forced - Immediate | 852-CC steam units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16547.0833 | 151 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U2-Forced - Delayed | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 287.8167 | 7 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 829.8666 | 128 | 2 | 2 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186.461 | 30.82 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365.8666 | 56 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 943.95 | 203 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 414.635 | 63.79 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1106 | 158 | 2 | 2 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 100-Fossil-Steam
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 861.6665 | 220 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 2722.5 | 242 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U2-Forced - Delayed | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 15082.1994 | 972 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 130.8333 | 50 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | D1-Forced - Immediate | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 2678.1332 | 242 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U2-Forced - Delayed | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U2 | Forced - Delayed | 2020 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Winter | 3060 | 272 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U2-Forced - Delayed | 850-Combined Cycle Block
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 467.496 | 64.93 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 851-CC GT units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | NPCC | Winter | 10121.8 | 221 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 851-CC GT units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 532.008 | 73.89 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 851-CC GT units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 852 | CC steam units | NPCC | Winter | 5862.4 | 128 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 852-CC steam units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 26.6 | 28 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 852-CC steam units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 699.78 | 98.1 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 852-CC steam units
3360 | Condensate makeup and return (including storage tanks) | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 260.7 | 237 | 1 | 1 | 3360-Condensate makeup and return (including storage tanks) | U1-Forced - Immediate | 852-CC steam units
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 921.1333 | 41 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 639.7733 | 73.82 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | U1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.9 | 21 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5833 | 11 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 588.4833 | 31 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1873.8667 | 16 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 100-Fossil-Steam
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1210.02 | 93.8 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 200-Nuclear
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 68.9 | 39 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | U1-Forced - Immediate | 830-Geothermal
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 874.2532 | 440.8 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | U1-Forced - Immediate | 850-Combined Cycle Block
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1788.3332 | 185 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | U1-Forced - Immediate | 851-CC GT units
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | U1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 1879.5 | 358 | 2 | 2 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | U1-Forced - Immediate | 851-CC GT units
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 364.6219 | 352.86 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 851-CC GT units
3370 | Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | Balance of Plant | Condensate System | D1 | Forced - Immediate | 2020 | Gas | GG | 851 | CC GT units | TRE | Summer | 351.3642 | 340.03 | 1 | 1 | 3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | D1-Forced - Immediate | 851-CC GT units